## Reading types dict.
Based on ReadingType IEC 61968-9 2023 recommendation
Index 1 | macroPeriod 宏周期 | Comments | Index 2 | aggregate 聚合方式 | Comments | Index 3 | measurePeriod 测量周期 | Comments | Index 4 | accumulationBehaviour 累加方式 | Comments | Index 5 | flowDirection 流动方向 | Comments | Index 6 | commodity 能源分类 | Comments | Index 7 | measurementKind 测量类别 | Comments | Index 8 | harmonic 谐波 | Comments | Index 9 | argumentNumerator 测量序号 | Comments | Index 10 | TOU 分时段号 | Comments | Index 11 | cpp 临界峰值 | Comments | Index 12 | Tier 分阶梯号 | Comments | Index 13 | Phase 相 | Comments | Index 14 | multiplier 公乘因子 | Comments | Index 15 | uom 统一计量单位 | Comments | Index 16 | currency 货币计量单位 | Comments
0 | 0.none | Not applicable. | 0 | 0.none | Not Applicable | 0 | 0.none | Not Applicable | 0 | 0.none | Not Applicable, or implied by the unit of measure. | 0 | 0.none | Not Applicable (N/A) | 0 | 0.none | Not Applicable | 0 | 0.none | Not Applicable | 0.0 | 0.0.none | Not Applicable | 0.0 | 0.0.none | Not Applicable | 0 | 0.none | Not Applicable | 0 | 0.none | Not Applicable | 0 | 0.none | Not applicable | 0 | 0.none | Not applicable to any phase | –24 | –24 .y | yocto = ×10–24 | 2 | 2.metre |  | 0 | 0.None | N
8 | 8.billingPeriod | Captured during the billing period starting at midnight of the first day of the billing period (as defined by the billing cycle day). If during the current billing period, it specifies a period from the start of the current billing period until "now". | 2 | 2.average |  | 1 | 1.tenMinute | 10 min | 1 | 1.bulkQuantity | A value from a register which represents the bulk quantity of a commodity. This quantity is computed as the integral of the commodity usage rate. This value is typically used as the basis for the dial reading at the meter, and as a result, will roll over upon reaching a maximum dial value. NOTE 1 With the metering system, the roll-over behaviour typically implies a roll-under behavior so that the value presented is always a positive value (e.g. unsigned integer or positive decimal.) However, when communicating data between enterprise applications a negative value might occur in a case such as net metering. NOTE 2 A BulkQuantity refers primarily to the dial reading and not the consumption over a specific period of time. | 1 | 1.forward |  | 1 | 1.electricity SecondaryMetered | All types of metered quantities. This type of reading comes from the meter and represents a “secondary” metered value. | 2 | 2.apparentPowerFactor | D | 1.2 | 1.2.interharmonic1/2 | Interharmonic of ½ | 1.2 | 1.2.n½ | One-half | 1 | 1.touA | Usage in the first defined TOU bucket | 1 | 1.cppA | Consumption associated with critical peak period A | 1 | 1.consumptionTier1 | Usage in the first defined consumption bucket | 16 | 16.phaseN | Neutral | –21 | –21 .z | zepto = ×10–21 | 3 | 3.gram |  | 36 | 36.AUD | Australian Dollar
11 | 11.daily | Daily period starting at midnight. If for the current day, this specifies the time from midnight to "now". | 4 | 4.excess | The value represents an amount over which a threshold was exceeded. | 2 | 2.fifteenMinute | 15 min | 2 | 2.continuousCumulative | The sum of the previous billing period values and the present period value. Note: “ContinuousCumulative” is commonly used in conjunction with “demand.” The “ContinuousCumulative Demand” would be the cumulative sum of the previous billing period maximum demand values (as occurring with each demand reset) summed with the present period maximum demand value (which has yet to be reset.) | 2 | 2.lagging | Typically used to describe that a power factor is lagging the reference value (or to say that the current is lagging the voltage.) NOTE 1 When used to describe power factor, the term “Lagging” implies that the PF is negative. The term “lagging” in this case takes the place of the negative sign. If a signed PF value is to be passed by the data producer, then the direction of flow enumeration zero (none) should be used in order to avoid the possibility of creating an expression that employs a double negative. The data consumer should be able to tell from the sign of the data if the PF is leading or lagging. This principle is analogous to the concept that “Reverse” energy is an implied negative value, and to publish a negative reverse value would be ambiguous. NOTE 2 Lagging power factors typically indicate inductive loading | 2 | 2.electricity PrimaryMetered | It is possible for a meter to be outfitted with an external VT and/or CT. The meter might not be aware of these devices, and the display not compensate for their presence. Ultimately, when these scalars are applied, the value that represents the service value is called the “primary metered” value. The “index” in sub-category 3 mirrors those of sub-category 0. | 3 | 3.currency | funds | 1.1 | 1.1.fundamental | fundamental | 0.1 | 0.1.n0 | “Zero” (for systems that use zero based numbering schemes) | 2 | 2.touB | Usage in the second defined TOU bucket | 2 | 2.cppB | Consumption associated with critical peak period B | 2 | 2.consumptionTier2 | Usage in the second defined consumption bucket | 17 | 17.phaseNtoGnd | Neutral to ground | –18 | –18 .a | atto = ×10–18 | 5 | 5.A | ampere | 124 | 124.CAD | Canadian Dollar
13 | 13.monthly | Monthly period starting at midnight on the first day of the month. If within the current month, this specifies the period from the start of the month until "now. | 5 | 5.highThreshold | The value represents a programmed threshold. | 3 | 3.oneMinute | 1 min | 3 | 3.cumulative | The sum of the previous billing period values. Note: “Cumulative” is commonly used in conjunction with “demand.” Each demand reset causes the maximum demand value for the present billing period (since the last demand reset) to accumulate as an accumulative total of all maximum demands. So instead of “zeroing” the demand register, a demand reset has the affect of adding the present maximum demand to this accumulating total. | 3 | 3.leading | Typically used to describe that a power factor is leading the reference value (or to say that the current is leading the voltage.) NOTE 3 Leading power factors typically indicate capacitive loading. | 3 | 3.communication | A measurement of the communication infrastructure itself. | 4 | 4.current | The flow of electrons | 2.1 | 2.1.harmonic2 | second harmonic | 1.1 | 1.1.n1 | "One,” where the measure needs an argument such as CEMI(n=1) | 3 | 3.touC | Usage in the third defined TOU bucket | 3 | 3.cppC | Consumption associated with critical peak period C | 3 | 3.consumptionTier3 | Usage in the third defined consumption bucket | 32 | 32.phaseC | Phase C | –15 | –15 .f | femto = ×10–15 | 6 | 6.K | Kelvin | 156 | 156.CNY | Chinese Yuan Renminbi
22 | 22.seasonal | A season of time spanning multiple months. E.g. "Summer," "Spring," "Fall," and "Winter" based cycle. If within the current season, it specifies the period from the start of the current season until "now." | 7 | 7.lowThreshold | The value represents a programmed threshold. | 4 | 4.twentyfourHour | 24 hour | 4 | 4.deltaData | The difference between the value at the end of the prescribed interval and the beginning of the interval. This is used for incremental interval data. NOTE 3 One common application would be for load profile data, another use might be to report the number of events within an interval (such as the number of equipment energizations within the specified period of time.) | 4 | 4.net | Defined as ¦Forward¦ - ¦Reverse¦, See IEC/TS 61968-2. NOTE 4 In some systems, the value passed as a “net” value could become negative. In other systems the value passed as a “net” value is always a positive number, and rolls-over and rolls-under as needed. | 4 | 4.air | N | 5 | 5.currentAngle | A phase current zerocross timing measurement releative to a reference voltage zerocross | 3.1 | 3.1.harmonic3 | third harmonic | 2.1 | 2.1.n2 | "Two" where the measure needs an argument such as CEMI(n=2) | 4 | 4.touD | Usage in the fourth defined TOU bucket | 4 | 4.cppD | Consumption associated with critical peak period D | 4 | 4.consumptionTier4 | Usage in the fourth defined consumption bucket | 33 | 33.phaseCtoN | Phase C to Neutral | –12 | –12 .p | pico = ×10–12 | 7 | 7.mole |  | 208 | 208.DKK | Danish Crown
24 | 24.weekly | Weekly period starting at midnight on the first day of the week and ending the instant before midnight the last day of the week. If within the current week, it specifies the period from the start of the week until "now." | 8 | 8.maximum | The highest value observed | 5 | 5.thirtyMinute | 30 min | 6 | 6.indicating | As if a needle is swung out on the meter face to a value to indicate the current value. (Note: An “indicating” value is typically measured over hundreds of milliseconds or greater, or may imply a “pusher” mechanism to capture a value. Compare this to “instantaneous” which is measured over a shorter period of time.) | 5 | 5.q1plusQ2 | Reactive positive quadrants. | 5 | 5.insulativeGas | (SF6 is found separately below.) | 6 | 6.currentImbalance | A measurement of the departure of a phase current relative to the average current of all phases | 4.1 | 4.1.harmonic4 | fourth harmonic | 3.1 | 3.1.n3 | "Three" where the measure needs an argument such as CEMI(n=3) | 5 | 5.touE | Usage in the fifth defined TOU bucket | 5 | 5.cppE | Consumption associated with critical peak period E | 5 | 5.consumptionTier5 | Usage in the fifth defined consumption bucket | 40 | 40.phaseCtoAv | Phase C current or voltage relative to Phase A voltage | –9 | –9 .n | nano = ×10–9 | 8 | 8.candela |  | 356 | 356.INR | India Rupee
32 | 32.specifiedPeriod | For the period defined by the start and end of the TimePeriod element in the message. | 9 | 9.minimum | The smallest value observed | 6 | 6.fiveMinute | 5 min | 9 | 9.summation | A form of accumulation which is selective with respect to time. NOTE 4 “Summation” could be considered a specialization of “Bulk Quantity” according to the rules of inheritance where “Summation” selectively accumulates pulses over a timing pattern, and “BulkQuantity” accumulates pulses all of the time. | 7 | 7.q1plusQ3 | Quadrants 1 and 3 | 6 | 6.insulativeOil | Typically mineral oil | 7 | 7.date | A measurement of the date and/or time in a clock, or a time stamp indicating when data was captured, when a maximum or minimum occurred, or to commemorate some other important aspect of a measurement | 5.1 | 5.1.harmonic5 | fifth harmonic | 4.1 | 4.1.n4 | "Four" where the measure needs an argument such as CEMI(n=4) | 6 | 6.touF | Usage in the sixth defined TOU bucket | 6 | 6.cppF | Consumption associated with critical peak period F | 6 | 6.consumptionTier6 | Usage in the sixth defined consumption bucket | 41 | 41.phaseCAtoN | CA to Neutral | –6 | –6 .µ | micro = ×10–6 | 27 | 27.second |  | 392 | 392.JPY | Japanese Yen
|  |  | 11 | 11.nominal |  | 7 | 7.sixtyMinute | 60 min | 10 | 10.timeDelay | A form of computation which introduces a time delay characteristic to the data value | 8 | 8.q1plusQ4 | Quadrants 1 and 4 usually represent forward active energy | 7 | 7.naturalGas | Naturally occurring hydrocarbon gas | 8 | 8.demand | The measurement of maximum power flow which is computed as energy usage over time, the dimensions of which are defined by a tariff | 6.1 | 6.1.harmonic6 | sixth harmonic | 5.1 | 5.1.n5 | "Five" where the measure needs an argument | 7 | 7.touG | Etc. | 7 | 7.cppG | Etc. | 7 | 7.consumptionTier7 | Additional consumption tiers may be created as necessary. | 64 | 64.phaseB | Phase B | –3 | –3 .m | milli= ×10–3 | 10 | 10.Radian (m/m) |  | 578 | 578.NOK | Norwegian Crown
|  |  | 12 | 12.normal |  | 10 | 10.twoMinute | 2 min | 12 | 12.instantaneous | Typically measured over the fastest period of time allowed by the definition of the metric (usually milliseconds or tens of milliseconds.) (Note: “Instantaneous” was moved to attribute #4 in 61968- 9Ed2 from attribute #1 in 61968-9:2009.) | 9 | 9.q1minusQ4 | Q1 minus Q4 | 8 | 8.propane | C3H8 | 9 | 9.distance | A linear distance or range radius | 7.1 | 7.1.harmonic7 | seventh harmonic | 6.1 | 6.1.n6 | Six | [9 empty] | 65 | 65.phaseBtoN | Phase B to Neutral | –2 | –2 .c | centi = ×10–2 | 11 | 11.Steradian (m2/m2) |  | 643 | 643.RUB | Russian Ruble
|  |  | 16 | 16.secondMaximum | The second highest value observed | 14 | 14.threeMinute | 3 min | 13 | 13.latchingQuantity | When this description is applied to a metered value, it implies that the value is a time-independent cumulative quantity much a BulkQuantity, except that it latches upon the maximum value upon reaching that value. Any additional accumulation (positive or negative) is discarded until a reset occurs. NOTE 5 A LatchingQuantity may also occur in the downward direction – upon reaching a minimum value. The terms “maximum” or “minimum” will usually be included as an attribute when this type of accumulation behaviour is present. When this description is applied to an encoded value (UOM= “Code”), it implies that the value has one or more bits which are latching. The condition that caused the bit to be set may have long since evaporated. In either case, the timestamp that accompanies the value may not coincide with the moment the value was initially set. In both cases a system will need to perform an operation to clear the latched value. | 10 | 10.q2plusQ3 | Quadrants 2 and 3 usually represent reverse active energy | 9 | 9.potableWater | Drinkable water | 10 | 10.distortionVoltAmperes | A measurement in which a V2 I2 term has both real and reactive components removed leaving only distortion. For example, distortion VAh = Sqrt( (V2h)(I2h) – (Wh)2 – (VArh)2) |  |  |  | 7.1 | 7.1.n7 | Seven | [9 empty] | 66 | 66.phaseBtoC | Phase B to C | –1 | –1 .d | deci = ×10–1 | 21 | 21.Gray (J/kg) |  | 710 | 710.ZAR | South African Rand
|  |  | 17 | 17.secondMinimum | The second smallest value observed | 15 | 15.present | Within the present period of time | 14 | 14.boundedQuantity | A time-independent cumulative quantity much a BulkQuantity or a LatchingQuantity, except that the accumulation stops at the maximum or minimum values. When the maximum is reached, any additional positive accumulation is discarded, but negative accumulation may be accepted (thus lowering the counter.) Likewise, when the negative bound is reached, any additional negative accumulation is discarded, but positive accumulation is accepted (thus increasing the counter.) | 11 | 11.q2plusQ4 | Quadrants 2 and 4 | 10 | 10.steam | Water in steam form, usually used for heating. | 11 | 11.energization | Pertaining to the presence of voltage |  |  |  | 8.1 | 8.1.n8 | Eight | [9 empty] | 72 | 72.phaseBtoAv | Phase B current or voltage relative to Phase A voltage | 0 | 0.Not applicable or "×1" | N | 22 | 22.Becquerel (1/s) |  | 752 | 752.SEK | Swedish Krona
|  |  | 23 | 23.thirdMaximum | The third highest value observed | 16 | 16.previous | Shifted within the previous monthly cycle and data set |  |  |  | 12 | 12.q2minusQ3 | Q2 minus Q3 | 11 | 11.wasteWater | (Sewerage) | 12 | 12.energy | Scalar quantity which may be increased or decreased in a system when it receives or produces work, respectively |  |  |  | 9.1 | 9.1.n9 | Nine | [9 empty] | 97 | 97.phaseBCtoN | BC to Neutral | 1 | 1.da | deca = ×101 | 23 | 23.degrees Celsius |  | 756 | 756.CHF | Swiss Franc
|  |  | 24 | 24.fourthMaximum | The fourth highest value observed | 31 | 31.twentyMinute | 20 min interval |  |  |  | 13 | 13.q3plusQ4 | Reactive negative quadrants. | 12 | 12.heatingFluid | This fluid is likely in liquid form. It is not necessarily water or water based. The warm fluid returns cooler than when it was sent. The heat conveyed may be metered. | 13 | 13.energizationLoadSide | Measuring the presence or absence of voltage on the load side of an electricity meter |  |  |  | 10.1 | 10.1.n10 | Ten | [9 empty] | 128 | 128.phaseA | Phase A | 2 | 2.h | hecto = ×102 | 24 | 24.Sievert (J/kg) |  | 826 | 826.GBP | British Pound
|  |  | 25 | 25.fifthMaximum | The fifth highest value observed | 50 | 50.fixedBlock60Min | 60 min Fixed Block |  |  |  | 14 | 14.q3minusQ2 | Q3 minus Q2 | 13 | 13.coolingFluid | The cool fluid returns warmer than when it was sent. The heat conveyed may be metered. | 14 | 14.fan | A forced air moving device |  |  |  | 15.1 | 15.1.n15 | Fifteen | [9 empty] | 129 | 129.phaseAtoN | Phase A to Neutral | 3 | 3.k | kilo = ×103 | 25 | 25.Farad (C/V) |  | 840 | 840.USD | US Dollar
|  |  | 26 | 26.sum | The accumulated sum | 51 | 51.fixedBlock30Min | 30 min Fixed Block |  |  |  | 15 | 15.quadrant1 |  | 14 | 14.nonpotableWater | Reclaimed water – possibly used for irrigation but not sufficiently treated to be considered safe for drinking. Moisture in oil | 15 | 15.frequency | Reciprocal of the period |  |  |  | 30.1 | 30.1.n30 | Thirty | [9 empty] | 132 | 132.phaseAtoB | Phase A to B | 6 | 6.M | Mega = ×106 | 26 | 26.Coulomb (Amp second) |  | 978 | 978.EUR | Euro
|  |  | 27 | 27.high | Typically used to identify the high volume flow port of a compound water meter. | 52 | 52.fixedBlock20Min | 20 min Fixed Block |  |  |  | 16 | 16.quadrant2 |  | 15 | 15.nox | Nitrous Oxides, NOX | 17 | 17.ieee1366ASAI | A measurement of IEEE-1366 Average Service Availability Index |  |  |  | 45.1 | 45.1.n45 | Fourtyfive | [9 empty] | 136 | 136.phaseAtoAv | Phase A current relative to Phase A voltage | 9 | 9.G | Giga = ×109 | 28 | 28.Henry (Wb/A)
|  |  | 28 | 28.low | Typically used to identify the low volume flow port of a compound water meter. | 53 | 53.fixedBlock15Min | 15 min Fixed Block |  |  |  | 17 | 17.quadrant3 |  | 16 | 16.so2 | Sulfur Dioxide, SO2 | 18 | 18.ieee1366ASIDI | A measurement of the IEEE-1366 Average Service Interruptio Duration Index |  |  |  | 60.1 | 60.1.n60 | Sixty | [9 empty] | 93 | 93.phaseABtoN | AB to Neutral | 12 | 12.T | Tera = ×1012 | 29 | 29.V | .Volt (W/A)
|  |  | 29 | 29.Standard Deviation Population | The standard deviation of a population (indicated by lower case sigma) | 54 | 54.fixedBlock10Min | 10 min Fixed Block |  |  |  | 18 | 18.quadrant4 |  | 17 | 17.ch4 | Methane, CH4 | 19 | 19.ieee1366ASIFI | A measurement of the IEEE-1366 Average Service Interruption Frequency Index |  |  |  | 120.1 | 120.1.n120 | 2 × 60 = 120 | [9 empty] | 224 | 224.phasesABC | Involving all phases | 15 | 15.P | Peta = ×1015 | 30 | 30.Ohm (V/A)
|  |  | 30 | 30.Standard Deviation Sample | The standard deviation of a sample drawn from a population (usually indicated by a lower case ‘s | 55 | 55.fixedBlock5Min | 5 min Fixed Block |  |  |  | 19 | 19.reverse |  | 18 | 18.co2 | Carbon Dioxide, CO2 | 20 | 20.ieee1366CAIDI | A measurement of the IEEE-1366 Customer averate interruption duration index |  |  |  | 155.1 | 155.1.n155 | One hundred fifty five | [9 empty] | 225 | 225.phaseABCtoN | ABC to Neutral | 18 | 18.E | Exa = ×1018 | 31 | 31.J | N·m = C·V = W·s
[6 empty] | 56 | 56.fixedBlock1Min | 1 min Fixed Bloc |  |  |  | 20 | 20.total | ¦Forward¦ + ¦Reverse¦, See IEC/TS 61968-2. The sum of the commodity in all quadrants Q1+Q2+Q3+Q4. In polyphase metering, the total energy register is incremented when the absolute value of the sum of the phase energies is greater than zero: ¦ EnergyA + EnergyB + EnergyC ¦ > 0 | 19 | 19.carbon | C | 21 | 21.ieee1366CAIFI | A measurement of the IEEE-1366 Customer average interruption frequency index |  |  |  | 240.1 | 240.1.n240 | 4 × 60 = 240 | [9 empty] | 256 | 256.s2 | Phase S2 | 21 | 21.Z | Zetta = ×1021 | 32 | 32.(kg m/s2)
[6 empty] | 57 | 57.rollingBlock60MinIntvl30MinSubIntvl | 60 min Rolling Block with 30-minute sub interval |  |  |  | 21 | 21.totalByPhase | In polyphase metering, the total by phase energy register is incremented when the sum of the absolute values of the phase energies is greater than zero: ¦ EnergyA ¦ + ¦ EnergyB ¦ + ¦ EnergyC ¦ > 0 In single phase metering, the formulas for “Total” and “Total by phase” collapse to the same expression. For communication purposes however, the “Total” enumeration should be used with single phase meter data. | 20 | 20.hch | Hexachlorocyclohexane, HCH | 22 | 22.ieee1366CEMIn | A measurement of the IEEE-1366 Customers Experiencing Multiple Interruptions |  |  |  | 305.1 | 305.1.n305 | Three hundred and five. | [9 empty] | 257 | 257.s2N | Phase S2 to Neutral | 24 | 24.Y | Yotta = ×1024 | 33 | 33.Hz | Cycles per second or (1/s)
[6 empty] | 58 | 58.rollingBlock60MinIntvl20MinSubIntvl | 60 min Rolling Block with 20-minute sub intervals | [6 empty] | 21 | 21.pfc | Perfluorocarbons, PFC | 23 | 23.ieee1366CEMSMIn | A measurement of the IEEE-1366 Customers Experiencing Multiple Sustained and Momentary Interruptions |  |  |  | 360.1 | 360.1.n360 | 6 × 60 = 360 | [9 empty] | 512 | 512.s1 | Phase S1 |  |  |  | 34 | 34.(lm/m2)
[6 empty] | 59 | 59.rollingBlock60MinIntvl15MinSubIntvl | 60 min Rolling Block with 15-minute sub intervals | [6 empty] | 22 | 22.sf6 | Sulfurhexafluoride, SF6 | 24 | 24.ieee1366CTAIDI | A measurement of the IEEE-1366 Customer Total Average Interruption Duration Index |  |  |  | 480.1 | 480.1.n480 | 8 × 60 = 480 | [9 empty] | 513 | 513.s1N | Phase S1 to Neutral |  |  |  | 35 | 35.lumen (cd sr)
[6 empty] | 60 | 60.rollingBlock60MinIntvl12MinSubIntvl | 60 min Rolling Block with 12-minute sub intervals | [6 empty] | 23 | 23.tvLicence | Television | 25 | 25.ieee1366MAIFI | A measurement of the IEEE-1366 Momentary Average Interruption Frequency Index |  |  |  | 720.1 | 720.1.n720 | 12 × 60 = 720 | [9 empty] | 768 | 768.s12 | Phase S1 to S2 |  |  |  | 36 | 36.Weber (V s)
[6 empty] | 61 | 61.rollingBlock60MinIntvl10MinSubIntvl | 60 min Rolling Block with 10-minute sub intervals | [6 empty] | 24 | 24.internet | Internet service | 26 | 26.ieee1366MAIFIe | A measurement of the IEEE-1366 Momentary Average event Interruption Frequency Index |  |  |  | 720.60 | 720.60.n720/60 | 12 × 60/1 × 60 | [9 empty] | 769 | 769.s12N | Phase S1, S2 to Neutral |  |  |  | 37 | 37.Tesla (Wb/m2)
[6 empty] | 62 | 62.rollingBlock60MinIntvl6MinSubIntvl | 60 min Rolling Block with 6-minute sub intervals | [6 empty] | 25 | 25.refuse | Trash | 27 | 27.ieee1366SAIDI | IEEE-1366 System Average Interruption Duration Index |  |  |  | 720.120 | 720.120.n720/120 | 12 × 60/2 × 60 | [9 empty] | 1248 | 1248.threeWireWye | 3W Wye |  |  |  | 38 | 38.W | Watt.
[6 empty] | 63 | 63.rollingBlock60MinIntvl5MinSubIntvl | 60 min Rolling Block with 5-minute sub intervals | [6 empty] | 26 | 26.h2 | Hydrogen, H2 | 28 | 28.ieee1366SAIFI | IEEE-1366 System Average Interruption Frequency Index |  |  |  | 720.180 | 720.180.n720/180 | 12 × 60/3 × 60 | [9 empty] | 1249 | 1249.fourWireWye | 4W Wye |  |  |  | 39 | 39.Pascal (N/m2)
[6 empty] | 64 | 64.rollingBlock60MinIntvl4MinSubIntvl | 60 min Rolling Block with 4-minute sub intervals | [6 empty] | 27 | 27.c2h2 | Acetylene, C2H2 | 31 | 31.lineLosses | An energy, power, voltage, or current loss attributed to transmission or distribution line impedance |  |  |  | 720.240 | 720.240.n720/240 | 12 × 60/4 × 60 | [9 empty] | 2272 | 2272.threeWireDelta | 3W Delta |  |  |  | 53 | 53.Siemens (A / V = 1 / Ω)
[6 empty] | 65 | 65.rollingBlock30MinIntvl15MinSubIntvl | 30 min Rolling Block with 15-minute sub intervals | [6 empty] | 28 | 28.c2h4 | Ethylene, C2H4 | 32 | 32.losses | A quantity lost due to “technical” reasons (such as line loss) or “non technical” reasons (such as theft.) |  |  |  | 720.360 | 720.360.n720/360 | 12 × 60/6 × 60 | [9 empty] | 2273 | 2273.fourWireDelta | 4W Delta |  |  |  | 155 | 155.PA | Pascal, absolute pressure
[6 empty] | 66 | 66.rollingBlock30MinIntvl10MinSubIntvl | 30 min Rolling Block with 10-minute sub intervals | [6 empty] | 29 | 29.c2h6 | Ethane, C2H6 | 33 | 33.negativeSequence | A quantity that has a rotation sequence which is opposite to that of the power system | [15 empty] | 6369 | 6369.fourWireHLDelta | 4W High-leg Delta |  |  |  | 140 | 140.PA | Pascal, gauge pressure
[6 empty] | 67 | 67.rollingBlock30MinIntvl6MinSubIntvl | 30 min Rolling Block with 6-minute sub intervals | [6 empty] | 30 | 30.co | Carbon monoxide, CO | 34 | 34.phasorPowerFactor | The ratio of real energy (usually net Wh) to phasor apparent energy (kVAh) | [15 empty] | 10465 | 10465.fourWireOpenDelta | 4W Open Delta |  |  |  | 158 | 158.katal = mol / s
[6 empty] | 68 | 68.rollingBlock30MinIntvl5MinSubIntvl | 30 min Rolling Block with 5-minute sub intervals | [6 empty] | 31 | 31.o2 | Oxygen, O2 | 35 | 35.phasorReactivePower | D | [15 empty] | 17153 | 17153.networked | Networked meter |  |  |  | 4 | 4.rotations per second
[6 empty] | 69 | 69.rollingBlock30MinIntvl3MinSubIntvl | 30 min Rolling Block with 3-minute sub intervals | [6 empty] | 32 | 32.dissolvedCombustibleGas | Dissolved Combustible Gas (A combination of combustible gasses such as H2, CH4, C2H2, C2H4, C 2H6, and/or CO in some mixture.) | 36 | 36.positiveSequence | A quantity that has a rotation sequence in agreement with that of the power system | [21 empty] | 41 | 41.square metre
[6 empty] | 70 | 70.rollingBlock30MinIntvl2MinSubIntvl | 30 min Rolling Block with 2-minute sub intervals | [6 empty] | 33 | 33.co2e | Carbon Dioxide CO2 Equivalent | 37 | 37.power | The derivative of energy with respect to time, where the energy is being transferred or transformed. | [21 empty] | 42 | 42.M³ | cubic metre
[6 empty] | 71 | 71.rollingBlock15MinIntvl5MinSubIntvl | 15 min Rolling Block with 5-minute sub intervals | [6 empty] | 34 | 34.lead | Lead, Pb | 38 | 38.powerFactor | The ratio of real energy (usually net kWh) to apparent energy (kVAh) | [21 empty] | 43 | 43.metre per second (m/s)
[6 empty] | 72 | 72.rollingBlock15MinIntvl3MinSubIntvl | 15 min Rolling Block with 3-minute sub intervals | [6 empty] | 35 | 35.mercury | Mercury, Hg | 40 | 40.quantityPower | A power measurement of Qh, where Qh is defined to be half of the sum of the Wh measurements on each phase plus the squareroot of 3 over two times the sum of the VArh measurements on each phase. | [21 empty] | 44 | 44.metre per second squared
[6 empty] | 73 | 73.rollingBlock15MinIntvl1MinSubIntvl | 15 min Rolling Block with 1-minute sub intervals | [6 empty] | 36 | 36.ozone | Ozone, O3 | 41 | 41.sag | A temporary dip in the supply voltage below the nominal value | [21 empty] | 45 | 45.cubic metres per second
[6 empty] | 74 | 74.rollingBlock10MinIntvl5MinSubIntvl | 10 min Rolling Block with 5-minute sub intervals | [6 empty] | 37 | 37.pm10 | Particulate matter whose maximum size is 10 µm. | 42 | 42.swell | A temporary rise of the supply voltage over the nominal value | [21 empty] | 46 | 46.metre / cubic metre
[6 empty] | 75 | 75.rollingBlock10MinIntvl2MinSubIntvl | 10 min Rolling Block with 2-minute sub intervals | [6 empty] | 38 | 38.pm25 | Particulate matter whose maximum size is 2,5 µm. | 43 | 43.switchPosition | A physical or logical switch position status which includes “opened” and “closed”, but for some products may also include “armed,” or other states that indicate a temporary state due to some condition. | [21 empty] | 47 | 47.kilogram metre (kg·m)
[6 empty] | 76 | 76.rollingBlock10MinIntvl1MinSubIntvl | 10 min Rolling Block with 1-minute sub intervals | [6 empty] | 39 | 39.sox | Sulfur Oxides, SOX | 44 | 44.tapPosition | Tap changer position | [21 empty] | 48 | 48.gram/cubic metre
[6 empty] | 77 | 77.rollingBlock5MinIntvl1MinSubIntvl | 5 min Rolling Block with 1-minute sub intervals | [6 empty] | 40 | 40.weather | Weather or meteorological conditions. | 45 | 45.tariffRate | An energy price defined in a contract. The rate might be a price for energy, for power (usually expressed as a demand value), or some other measurement. The rate might be currency based, or as a code, or as a component of a larger tariff description. | [21 empty] | 49 | 49.metre squared / second
[6 empty] | 78 | 78.twelveMinute | 12 min | [6 empty] | 41 | 41.device | Condition of the meter or end device itself. For example, this enumeration might be used in combination with an enumeration for temperature to represent the internal temperature of a meter. | 46 | 46.temperature | A quantity proportional to the energy of a system | [21 empty] | 50 | 50.Watt/metre Kelvin
[6 empty] | 79 | 79.twoHour | 2 h | [6 empty] | 42 | 42.pole | The power pole as an end device | 47 | 47.totalHarmonicDistortion | The ratio of the sum of the harmonics to the fundamental. (THD may measure either voltage or current, and may isolated to a given phase) | [21 empty] | 51 | 51.Joule/Kelvin
[6 empty] | 80 | 80.fourHour | 4 h | [6 empty] | 43 | 43.conductor | A wire as an end device | 48 | 48.transformerLosses | A measurement of the energy or power loss in a transformer due to inefficiency | [21 empty] | 54 | 54.radians per second
[6 empty] | 81 | 81.sixHour | 6 h | [6 empty] | 44 | 44.acceleration | A measurement of acceleration | 49 | 49.unipedeVoltageDip10to15 | A voltage dip classification per EN50160 or a similar national standard measuring the number of dips in the 10-15% range | [21 empty] | 61 | 61.VA | Volt Ampere
[6 empty] | 82 | 82.twelveHour | 12 h | [6 empty] | 45 | 45.tilt | A measurement of tilt | 50 | 50.unipedeVoltageDip15to30 | A voltage dip classification per EN50160 or a similar national standard measuring the number of dips in the 15-30% range | [21 empty] | 63 | 63.var | Volt Ampere reactive
[6 empty] | 83 | 83.threeHour | 3 h | [6 empty] | 46 | 46.magneticField | A measurement of the magnetic field | 51 | 51.unipedeVoltageDip30to60 | A voltage dip classification per EN50160 or a similar national standard measuring the number of dips in the 30-60% range | [21 empty] | 66 | 66.Volt seconds (Ws/A)
[6 empty] | 100 | 100.specifiedInterval | The interval length is described in attribute #10 in seconds. Attribute #11 should be "1" for whole seconds. | [6 empty] | 50 | 50.Gas | Generic commodity for gas. Note that there are specific commodities for natural gas and propane. | 52 | 52.unipedeVoltageDip60to90 | A voltage dip classification per EN50160 or a similar national standard measuring the number of dips in the 60-90% range | [21 empty] | 67 | 67.Volt squared (W2/A2)
[6 empty] | 101 | 101.specifiedFixedBlock | The fixed block duration is described in attribute #10 in seconds. Attribute #11 should be "1" for whole seconds. | [6 empty] | 60 | 60.Water | Generic commodity for water. Note that there are specific commodities for waste water and potable water. | 53 | 53.unipedeVoltageDip90to100 | A voltage dip classification per EN50160 or a similar national standard measuring the number of dips in the 90-100% range | [21 empty] | 68 | 68.Amp seconds
[6 empty] | 102 | 102.specifiedRollingBlock | The rolling block size is described by attribute #10 in seconds, and the sub-interval size by attribute #11 in seconds. | [6 empty] | 901 | 901.electricity DirectMetered | All types of metered quantities. This type of reading comes from the meter and represents a “DC” metered value. | 54 | 54.Voltage (rms) | The difference in electric potential between two points | [21 empty] | 69 | 69.Amp squared
[15 empty] | 902 | 902.BMS of Storage | All types of BMS of Storage | 55 | 55.voltageAngle | A phase voltage zerocross timing measurement releative to a reference voltage zerocross | [21 empty] | 70 | 70.square Amp second
[15 empty] | 903 | 903 PCS of Storage | All types of PCS of Storage | 56 | 56.voltageExcursion | A measurement of the departure of the voltage from the nominal voltage | [21 empty] | 71 | 71.Vah | Volt Ampere hours
[15 empty] | 904 | 904 Monitor of Storage | All types of Monitor of Storage | 57 | 57.voltageImbalance | A measurement of the departure of a phase voltage relative to the average voltage of all phases. | [21 empty] | 72 | 72.W·h | Watt hours
[18 empty] | 58 | 58.volume | fluid volume | [21 empty] | 73 | 73.varh | Volt Ampere reactive hours
[18 empty] | 59 | 59.zeroFlowDuration | The amount of time that current flow drops to a zero level or level below the ability of the sensor to sense | [21 empty] | 74 | 74.Volt per Hertz
[18 empty] | 60 | 60.zeroSequence | The zero sequence current is the vector sum of the phase currents | [21 empty] | 75 | 75.Hertz per second
[18 empty] | 64 | 64.distortionPowerFactor | The ratio of the distortion VAh to the apparent VAh | [21 empty] | 78 | 78.kg m2
[18 empty] | 81 | 81.frequencyExcursion | A measurement of the departure of the frequency from the nominal frequency | [21 empty] | 81 | 81.Watt per second
[18 empty] | 90 | 90.applicationContext | Information that describes the logical context in which a request, measurement, or command is made. | [21 empty] | 82 | 82.litre per second
[18 empty] | 91 | 91.apTitle | An application name which is making or has made a request | [21 empty] | 100 | 100.Q
[18 empty] | 92 | 92.assetNumber | An asset identifier | [21 empty] | 101 | 101.Qh
[18 empty] | 93 | 93.bandwidth | A measurement of dataflow | [21 empty] | 102 | 102.Ohm metre, ρ (rho)
[18 empty] | 94 | 94.batteryVoltage | Battery voltage | [21 empty] | 103 | 103.magnetic field strength, Ampere per metre
[18 empty] | 95 | 95.broadcastAddress | A message target address implying all endpoint units within range of a particular sender | [21 empty] | 104 | 104.Volt-squared-hours
[18 empty] | 96 | 96.deviceAddressType1 | Endpoint target address Type1 | [21 empty] | 105 | 105.Ampere-squared hour
[18 empty] | 97 | 97.deviceAddressType2 | Endpoint target address Type2 | [21 empty] | 106 | 106.Ah | Ampere-hours
[18 empty] | 98 | 98.deviceAddressType3 | Endpoint target address Type3 | [21 empty] | 107 | 107.energy per volume
[18 empty] | 99 | 99.deviceAddressType4 | Endpoint target address Type4 | [21 empty] | 108 | 108.time and date per ISO 8601 format
[18 empty] | 100 | 100.deviceClass | A unique identifier for the Endpoint’s configuration | [21 empty] | 115 | 115.active energy metering constant
[18 empty] | 101 | 101.electronicSerialNumber | A device serial number | [21 empty] | 116 | 116.reactive energy metering constant
[18 empty] | 102 | 102.endDeviceID | A unique identifier of the endDevice – the device providing measurements or under control of the network | [21 empty] | 117 | 117.apparent energy metering constant
[18 empty] | 103 | 103.groupAddressType1 | Group target address Type1 | [21 empty] | 125 | 125.cubic metre per hour
[18 empty] | 104 | 104.groupAddressType2 | Group target address Type2 | [21 empty] | 126 | 126.compensated cubic metre per hour
[18 empty] | 105 | 105.groupAddressType3 | Group target address Type3 | [21 empty] | 127 | 127.uncompensated cubic metre per hour
[18 empty] | 106 | 106.groupAddressType4 | Group target address Type4 | [21 empty] | 137 | 137.L/h | litre per hour
[18 empty] | 107 | 107.ipAddress | An IP address for the endpoint | [21 empty] | 139 | 139.litre (uncompensated) per hour
[18 empty] | 108 | 108.macAddress | A MAC address for the endpoint | [21 empty] | 138 | 138.litre (compensated) per hour
[18 empty] | 109 | 109.mfgAssignedConfigurationID | The at time of manufacture configuration given to a device | [21 empty] | 161 | 161.Q measured at 45º
[18 empty] | 110 | 110.mfgAssignedPhysicalSerialNumber | The serial number assigned to a device at time of manufacture | [21 empty] | 162 | 162.Q measured at 60º
[18 empty] | 111 | 111.mfgAssignedProductNumber | The product number assigned to a device at time of manufacture | [21 empty] | 163 | 163.Qh measured at 45º
[18 empty] | 112 | 112.mfgAssignedUniqueCommunicationAddress | A communication address assigned to a device at time of manufacture | [21 empty] | 164 | 164.Qh measured at 60º
[18 empty] | 113 | 113.multiCastAddress | A message target address implying a large group of endpoint units within range of a particular sender | [21 empty] | 165 | 165.Joule / kg
[18 empty] | 114 | 114.oneWayAddress | A communication address of a network endpoint used in one-way communication | [21 empty] | 166 | 166.cubic metre, with the value uncompensated for weather effects.
[18 empty] | 115 | 115.signalStrength | A measurement of RF signal strength | [21 empty] | 167 | 167.cubic metre, with the value compensated for weather effects.
[18 empty] | 116 | 116.twoWayAddress | A communication address used for bidirectional communication | [21 empty] | 173 | 173.reciprocal metre, (1/m)
[18 empty] | 117 | 117.signaltoNoiseRatio | A measurement of received (RF) signal strength divided by the (RF) noise floor | [21 empty] | 174 | 174.cubic metre per kilogram, v
[18 empty] | 118 | 118.alarm | A measurement releated to an alarm | [21 empty] | 175 | 175.Pascal second
[18 empty] | 119 | 119.batteryCarryover | An estimate of the battery ridethrough capacity | [21 empty] | 176 | 176.Newton metre
[18 empty] | 120 | 120.dataOverflowAlarm | An indication of or measurement of a loss of data | [21 empty] | 177 | 177.Newton per metre
[18 empty] | 121 | 121.demandLimit | A threshold setting that determines the trip point that if exceeded would trigger a demand limiting action or alarm | [21 empty] | 178 | 178.radian per second squared
[18 empty] | 122 | 122.demandReset | A count of the number of times demand has been reset (remotely, locally, and/or automatically.) | [21 empty] | 179 | 179.Watt per square metre
[18 empty] | 123 | 123.diagnostic | A measurement releated to equipment diagnostics | [21 empty] | 180 | 180.Joule per kilogram kelvin
[18 empty] | 124 | 124.emergencyLimit | A setting that indicates an emergency limit | [21 empty] | 181 | 181.Joule per cubic metre
[18 empty] | 125 | 125.encoderTamper | An indication of tampering with a meter encoder | [21 empty] | 182 | 182.Volt per metre
[18 empty] | 126 | 126.ieee1366MomentaryInterruption | IEEE-1366 Momentary Interruption count | [21 empty] | 183 | 183.Coulomb per cubic metre
[18 empty] | 127 | 127.ieee1366MomentaryInterruptionEvent | IEEE-1366 Momentary Interruption event count | [21 empty] | 184 | 184.Coulomb per square metre
[18 empty] | 128 | 128.ieee1366SustainedInterruption | IEEE-1366 Sustained Interruption duration | [21 empty] | 185 | 185.Farad per metre
[18 empty] | 129 | 129.interruptionBehaviour | A measurement related to power interruptions (Note: often an interruption count or duration.) | [21 empty] | 186 | 186.Henry per metre
[18 empty] | 130 | 130.inversionTamper | A measurement related to inversion tamper (Note: typically a count of inversions) | [21 empty] | 187 | 187.Joule per mole
[18 empty] | 131 | 131.loadInterrupt | A measurement related to load interruption (Note: typically a load interruption count or measurement of duration) | [21 empty] | 188 | 188.Joule per mole kelvin
[18 empty] | 132 | 132.loadShed | A measurement related to load shed (Note: typically a load shed count or load shed duration) | [21 empty] | 189 | 189.Coulomb per kilogram
[18 empty] | 133 | 133.maintenance | A measurement related to the pending maintenance of equipment | [21 empty] | 190 | 190.Gray per second
[18 empty] | 134 | 134.physicalTamper | A measurement related to physical tampering (Note: typically a tamper count) | [21 empty] | 191 | 191.Watt per steradian
[18 empty] | 135 | 135.powerLossTamper | Tamper indicated while power was out | [21 empty] | 192 | 192.Watt per square metre steradian
[18 empty] | 136 | 136.powerOutage | A measurement related to power outages (Note: typically a status) | [21 empty] | 193 | 193.katal per cubic metre
[18 empty] | 137 | 137.powerQuality | A measurement related to power quality | [21 empty] | 280 | 280.Volt hours
[18 empty] | 138 | 138.powerRestoration | A measurement related to power restoration (Note: typically a status) | [21 empty] | 159 | 159.minute = 60 s
[18 empty] | 139 | 139.programmed | A measurement related to device programming (Note: typically a status measurement) | [21 empty] | 160 | 160.hour = 60 min = 3 600 s
[18 empty] | 140 | 140.pushbutton | A measurement related to pushbutton (Note: typically a status or count) | [21 empty] | 195 | 195.day = 24 h = 86 400 s
[18 empty] | 141 | 141.relayActivation | A measurement related to relay activations | [21 empty] | 9 | 9.degree
[18 empty] | 142 | 142.relayCycle | A measurement related to relay cycling (Note1: one open and one closure together is one cycle, Note2: Usually expressed as a count) | [21 empty] | 196 | 196.minute
[18 empty] | 143 | 143.removalTamper | An indication of equipment tampering that shows equipment was moved or opened | [21 empty] | 197 | 197.second
[18 empty] | 144 | 144.reprogrammingTamper | An indication of equipment tampering that shows equipment has been reprogrammed | [21 empty] | 198 | 198.hectare
[18 empty] | 145 | 145.reverseRotationTamper | An indication of tampering as evidenced by reverse power flow | [21 empty] | 134 | 134.L | litre = dm3 = m3/1 000
[18 empty] | 146 | 146.switchArmed | A measurement of the switch arm condition | [21 empty] | 199 | 199.“tonne” or “metric ton” (1 000 kg = 1 Mg)
[18 empty] | 147 | 147.switchDisabled | A measurement of the switch enablement status | [21 empty] | 0 | 0.N/A
[18 empty] | 148 | 148.tamper | An indication of equipment tampering | [21 empty] | 65 | 65.Cosφ | Power factor
[18 empty] | 149 | 149.watchdogTimeout | A reset triggered by a hardware “watchdog” circuit | [21 empty] | 79 | 79.Logrithmic ratio
[18 empty] | 150 | 150.billLastPeriod | Customer’s bill for the previous billing period Expressed as currency. | [21 empty] | 109 | 109.State
[18 empty] | 151 | 151.billToDate | Customer’s bill, as known thus far within the present billing period. Expressed as currency. | [21 empty] | 111 | 111.Amount of substance
[18 empty] | 152 | 152.billCarryover | Customer’s bill, part of a previous obligation carried over from a previous billing period. Expressed as currency. | [21 empty] | 113 | 113.Logrithmic ratio of signal strength
[18 empty] | 153 | 153.connectionFee | Monthly fee for connection to commodity. | [21 empty] | 114 | 114.Application Value
[18 empty] | 154 | 154.audibleVolume | Sound | [21 empty] | 118 | 118.EndDeviceEvent
[18 empty] | 155 | 155.volumetricFlow | A fluid flow rate | [21 empty] | 143 | 143.Concentration
[18 empty] | 156 | 156.relativeHumidity | Most common usage is in expressing weather or meteorological conditions | [21 empty] | 144 | 144.Concentration
[18 empty] | 157 | 157.skyCover | Degree of sky cover. Used in expressing weather or meteorological conditions. | [21 empty] | 145 | 145.Concentration
[18 empty] | 158 | 158.voltage | Unspecified | [21 empty] | 146 | 146.Concentration
[18 empty] | 159 | 159.dcVoltage | I | [21 empty] | 147 | 147.Molality
[18 empty] | 160 | 160.acVoltagePeak | Vp=√2 × Vrms | [21 empty] | 148 | 148.Ratio of length
[18 empty] | 161 | 161.acVoltagePeakToPeak | Vpp=2 × Vp | [21 empty] | 149 | 149.Ratio of time
[18 empty] | 162 | 162.pressure | Force over area | [21 empty] | 150 | 150.Rate of frequency change
[18 empty] | 163 | 163.density | I | [21 empty] | 151 | 151.Ratio of voltages
[18 empty] | 164 | 164.energyDensity | I | [21 empty] | 152 | 152.Ratio of Amperages
[18 empty] | 165 | 165.dateOfLastDemandReset | I | [21 empty] | 153 | 153.PF, the ratio of the active power to the apparent power.
[18 empty] | 166 | 166.arithmeticApparentEnergy | The arithmetic sum of the per element VAh quantities, where each element apparent VAh uantity is calculated each momentary interval as: sqrt(V2hx)(I2hx), where x= each element A, B, C, and V2hx and I2hx are fundamental plus harmonics values. | [21 empty] | 154 | 154.Revolutions
[18 empty] | 167 | 167.arithmeticApparentPower | The rate of arithmetic Apparent Energy | [21 empty] | 168 | 168.Ratio of power
[18 empty] | 168 | 168.arithmeticApparentDemand | I | [21 empty] | 170 | 170.n
[18 empty] | 169 | 169.phasorApparentEnergy | Sqrt((Whx)2+(VArhx)2) where x each element A,B,C and VArh is measured with IEEE VArs | [21 empty] | 171 | 171.μr
[18 empty] | 170 | 170.phasorApparentPower | The rate of phasor apparent energy | [21 empty] | 172 | 172.Neper
[18 empty] | 171 | 171.phasorApparentDemand | I | [21 empty] | 281 | 281.Relative humidity
[18 empty] | 172 | 172.distortionApparentEnergy | distortion VAhx = Sqrt( (V2hx)(I2hx) – (Whx)2 – (VArhx)2), where x= each element A, B, or C and V2hx, I2hx, Whx, and varhx are fundamental plus harmonic values | [21 empty] | 282 | 282.Ratio of covered sky to total sky.
[18 empty] | 173 | 173.distortionApparentPower | The rate of distortion apparent energy | [21 empty] | 200 | 200.electronvolt
[18 empty] | 174 | 174.distortionApparentDemand | Distoration apparent energy passed through a demand function | [21 empty] | 201 | 201.dalton
[18 empty] | 175 | 175.totalHarmonicDistortionDemand | THD treated as a demand | [21 empty] | 202 | 202.unified atomic mass unit
[18 empty] | 176 | 176.tddDemand | Total Demand Distortion treated as a demand | [21 empty] | 203 | 203.astronomical unit (1ua = 1,495 978 × 1011 m)
[18 empty] | 177 | 177.totalDemandDistortion | (RMS of harmonic content of current) / (maximum installation current) | [21 empty] | 204 | 204.natural unit of speed (speed of light in a vacuum)
[18 empty] | 178 | 178.distortionPowerFactorDemand | distortionPF treated as a demand value | [21 empty] | 205 | 205.natural unit of action (reduced planck constant)
[18 empty] | 179 | 179.fuzzyEnergy | Fuzzyvarh = sqrt((varh)2 + (distortion VAh)2), where varh is a fundamental plus harmonics value | [21 empty] | 206 | 206.natural unit of mass (electron mass)
[18 empty] | 180 | 180.fuzzyPower | The rate of fuzzy energy | [21 empty] | 207 | 207.natural unit of time
[18 empty] | 181 | 181.fuzzyDemand | Fuzzy energy as a demand | [21 empty] | 208 | 208.atomic units of charge (elementary charge)
[18 empty] | 183 | 183.batteryChargeMoved | Charge used or added | [21 empty] | 209 | 209.atomic units of mass (electron mass)
[18 empty] | 184 | 184.batteryChargeStored | Charge present | [21 empty] | 210 | 210.atomic unit of action (reduced planck constant)
[18 empty] | 188 | 188.quadrant | One of four quadrants relative to the reference axix | [21 empty] | 211 | 211.atomic unit of length, bohr ( Bohr radius)
[18 empty] | 189 | 189.processorReset | The type of reset | [21 empty] | 212 | 212.atomic unit of energy, hartree
[18 empty] | 190 | 190.xAxis | Measurement along the x axis relative to the reference axis | [21 empty] | 213 | 213.atomic unit of time
[18 empty] | 191 | 191.yAxis | Measurement along the y axis | [21 empty] | 76 | 76.characters
[18 empty] | 192 | 192.zAxis | Measurement along the z axis | [21 empty] | 77 | 77.characters per second
[18 empty] | 193 | 193.XYPlane | Measurement in the XY Plane | [21 empty] | 80 | 80.Generic money
[18 empty] | 194 | 194.YZPlane | Measurement in the YZ Plane | [21 empty] | 119 | 119.cubic foot
[18 empty] | 195 | 195.XZPlane | Measurement in the XZ Plane | [21 empty] | 120 | 120.cubic foot compensated for weather
[18 empty] | 901 | SOC | State of Charge | [21 empty] | 121 | 121.cubic foot uncompensated for weather
[18 empty] | 902 | SOH | State of Health | [21 empty] | 122 | 122.cubic foot per hour
[18 empty] | 903 | efficiency | efficiency | [21 empty] | 123 | 123.compensated cubic feet per hour
[18 empty] | 904 | ControlMode | ControlMode | [21 empty] | 124 | 124.uncompensated cubic feet per hour
[42 empty] | 128 | 128.US gallon (1 gal = 231 in3 = 128 fl oz.)
[42 empty] | 129 | 129.US gallon per hour
[42 empty] | 130 | 130.Imperial gallon
[42 empty] | 131 | 131.Imperial gallon per hour
[42 empty] | 132 | 132.British Thermal Unit
[42 empty] | 133 | 133.BTU per hour
[42 empty] | 141 | 141.Pound per square inch, absolute
[42 empty] | 142 | 142.Pound per square inch, gauge
[42 empty] | 156 | 156.Litre, with the value uncompensated for weather effects
[42 empty] | 157 | 157.Litre, with the value compensated for weather effects
[42 empty] | 169 | 169.Therm
[42 empty] | 214 | 214.bar (1 bar = 100 kPa)
[42 empty] | 215 | 215.millimeter of mercury (1 mmHg ≈ 133,3 Pa)
[42 empty] | 216 | 216.ångström (1Å = 10–10 m)
[42 empty] | 217 | 217.nautical mile (1 M = 1852 m)
[42 empty] | 218 | 218.barn (1 b = 100 fm2 = 10–28 m2)
[42 empty] | 219 | 219.knot (1 kn = 1852/3600) m/s
[42 empty] | 220 | 220.curie (1 Ci = 3,7 × 1010 Bq)
[42 empty] | 221 | 221.roentgen (1 R = 2,58 × 10–4 C/kg)
[42 empty] | 222 | 222.rad (1 rd = 1 cGy)
[42 empty] | 223 | 223.rem (1 rem = 10–2 Sv)
[42 empty] | 224 | 224.inch
[42 empty] | 225 | 225.foot (1 ft = 12 in)
[42 empty] | 226 | 226.rod (1 rod = 16,5 ft)
[42 empty] | 227 | 227.furlong (1 fur = 660 ft)
[42 empty] | 228 | 228.mile (1 statute mile = 8 fur = 80 chains = 320 rods = 5280
[42 empty] | 229 | 229.square foot (1 ft2 = 144 in2)
[42 empty] | 230 | 230.square yard (1 yd2 = 9 ft2)
[42 empty] | 231 | 231.square rod (1 rod2 = 272,25 ft2)
[42 empty] | 232 | 232.acre (1 acre = 160 rd2 = 43 560 ft2)
[42 empty] | 233 | 233.square mile (1 mi2 = 640 acres)
[42 empty] | 234 | 234.section of land (1 mi2 = 1 section of land)
[42 empty] | 235 | 235.township (1 township = 6 miles square)
[42 empty] | 237 | 237.cubic yard (1 yd3 = 27 ft3)
[42 empty] | 238 | 238.link (1 li = 0,66 ft)
[42 empty] | 239 | 239.chain (1 ch = 100 links = 4 rods = 66 ft)
[42 empty] | 240 | 240.US liquid pint (1 pt = 28,875 in3 = 128 fl dr)
[42 empty] | 241 | 241.US liquid quart (1 qt = 2 pt)
[42 empty] | 242 | 242.Apothecaries fluid dram
[42 empty] | 243 | 243.Apothecaries fluid ounce (1 fl oz ap = 8 fl dr ap)
[42 empty] | 244 | 244.US dry pint (1 pt = 67,2 in3)
[42 empty] | 245 | 245.US dry quart (1 qt = 2 pints)
[42 empty] | 246 | 246.US peck (1 pk = 8 qt)
[42 empty] | 247 | 247.US bushel (1 bu = 4 pk)
[42 empty] | 248 | 248.grain (1 grain = 1/7000 avdp lb)
[42 empty] | 249 | 249.Avoirdupois dram (1 Avdp dr = 27-11/32 gr)
[42 empty] | 250 | 250.Avoirdupois ounce (1 Avdp oz = 16 Avdp dr)
[42 empty] | 251 | 251.Avoirdupois pound (1 lb = 16 oz)
[42 empty] | 252 | 252.Avoirdupois hundredweight (1 cwt = 100 lbs)
[42 empty] | 253 | 253.Avoirdupois ton (1 short ton = 2000 lbs)
[42 empty] | 254 | 254.Avoirdupois gross or long hundredweight
[42 empty] | 255 | 255.Avoirdupois gross or long ton
[42 empty] | 256 | 256.Troy pennyweight (1 dwt = 24 grains)
[42 empty] | 257 | 257.Troy ounce (1 oz t = 20 dwt)
[42 empty] | 258 | 258.Troy pound (1 lb t = 12 oz t)
[42 empty] | 259 | 259.Apothecaries scruple (1 s ap = 20 grains)
[42 empty] | 260 | 260.Apothecaries dram (1 dr ap = 3 s ap)
[42 empty] | 261 | 261.Apothecaries ounce (1 oz ap = 8 dr ap)
[42 empty] | 262 | 262.Apothecaries pound (1 lp ap = 12 oz ap)
[42 empty] | 263 | 263.mile per imperial gallon
[42 empty] | 264 | 264.mile per US gallon
[42 empty] | 265 | 265.mile per US gallon equivalent
[42 empty] | 266 | 266.litre per 100 km
[42 empty] | 267 | 267.killowatt-hour per mile
[42 empty] | 268 | 268.kilowatt-hour per 100 mile
[42 empty] | 279 | 279.degrees Fahrenheit
[42 empty] | 269 | 269.erg (1 erg = 10–7 J)
[42 empty] | 270 | 270.dyne (1 dyn = 10–5 N)
[42 empty] | 271 | 271.poise (1 P = 0,1 Pa s)
[42 empty] | 272 | 272.stokes (1 St = 1 cm2/s)
[42 empty] | 273 | 273.stilb (1 sb = 104 cd/m2)
[42 empty] | 274 | 274.phot (1 ph = 104 lx)
[42 empty] | 275 | 275.gal (1 Gal = 10–2 m s–2)
[42 empty] | 276 | 276.Maxwell (1 Mx = 10–8 Wb)
[42 empty] | 277 | 277.Gauss (1 G = 10–4 T)
[42 empty] | 278 | 278.OErsted (1 Oe = (103/4π) A/m)
[42 empty] | 278 | 278.278.Œrsted (1 Oe = (103/4π) A/m)
[42 empty] | 801 | %
[42 empty] | 802 | RMB

## ReadingTypeID表计
mRID | [15 empty] | KAIFA Project | EMS-01 | ReadingType
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | mRID | Description | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
mRID | [17 empty] | macroPeriod 宏周期 | aggregate 聚合方式 | measurePeriod 测量周期 | accumulationBehaviour 累加方式 | flowDirection 流动方向 | commodity 能源分类 | measurementKind 测量类别 | harmonic 谐波 | argument 测量序号 | TOU 分时段号 | CPP 临界峰值 | Tier 分阶梯号 | Phase 相 | multiplier 公乘因子 | uom 统一计量单位 | currency 货币计量单位
0 | 0 | 2 | 4 | 1 | 1 | 12 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.2.4.1.1.12.0.0.0.0.0.0.0.0.3.72.0 | 15分钟正向间隔有功电能（k·Wh） | 0.none | 0.none | 2.fifteenMinute | 4.deltaData | 1.forward | 1.electricity SecondaryMetered | 12.energy | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 2 | 4 | 19 | 1 | 12 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.2.4.19.1.12.0.0.0.0.0.0.0.0.3.72.0 | 15分钟反向间隔有功电能（k·Wh） | 0.none | 0.none | 2.fifteenMinute | 4.deltaData | 19.reverse | 1.electricity SecondaryMetered | 12.energy | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 6 | 4 | 1 | 1 | 12 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.6.4.1.1.12.0.0.0.0.0.0.0.0.3.72.0 | 5分钟间隔正向有功电能（k·Wh） | 0.none | 0.none | 6.fiveMinute | 4.deltaData | 1.forward | 1.electricity SecondaryMetered | 12.energy | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 6 | 4 | 19 | 1 | 12 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.6.4.19.1.12.0.0.0.0.0.0.0.0.3.72.0 | 5分钟间隔反向有功电能（k·Wh） | 0.none | 0.none | 6.fiveMinute | 4.deltaData | 19.reverse | 1.electricity SecondaryMetered | 12.energy | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 2 | 4 | 4 | 1 | 12 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.2.4.4.1.12.0.0.0.0.0.0.0.0.3.72.0 | 15分钟间隔净有功电能（k·Wh） | 0.none | 0.none | 2.fifteenMinute | 4.deltaData | 4.net | 1.electricity SecondaryMetered | 12.energy | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 6 | 4 | 4 | 1 | 12 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.6.4.4.1.12.0.0.0.0.0.0.0.0.3.72.0 | 5分钟间隔净有功电能（k·Wh） | 0.none | 0.none | 6.fiveMinute | 4.deltaData | 4.net | 1.electricity SecondaryMetered | 12.energy | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 0 | 3 | 1 | 1 | 12 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.0.3.1.1.12.0.0.0.0.0.0.0.0.3.72.0 | 总正向累计有功电能（k·Wh） | 0.none | 0.none | 0.none | 3.cumulative | 1.forward | 1.electricity SecondaryMetered | 12.energy | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 0 | 3 | 19 | 1 | 12 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.0.3.19.1.12.0.0.0.0.0.0.0.0.3.72.0 | 总反向累计有功电能（k·Wh） | 0.none | 0.none | 0.none | 3.cumulative | 19.reverse | 1.electricity SecondaryMetered | 12.energy | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 0 | 3 | 4 | 1 | 12 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.0.3.4.1.12.0.0.0.0.0.0.0.0.3.72.0 | 总正向累计净电能（k·Wh） | 0.none | 0.none | 0.none | 3.cumulative | 4.net | 1.electricity SecondaryMetered | 12.energy | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 15 | 0 | 0 | 1 | 158 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0.0.15.0.0.1.158.0.0.0.0.0.0.0.0.0.29.0 | 单相表当前电压（V） | 0.none | 0.none | 15.present | 0.none | 0.none | 1.electricity SecondaryMetered | 158.voltage | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 29.V | 0.None
0 | 0 | 15 | 0 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 38 | 0 | 0.0.15.0.1.1.37.0.0.0.0.0.0.0.0.3.38.0 | 单相表当前正向功率（kW） | 0.none | 0.none | 15.present | 0.none | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 38.W | 0.None
0 | 0 | 15 | 0 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 38 | 0 | 0.0.15.0.4.1.37.0.0.0.0.0.0.0.0.3.38.0 | 单相表当前净功率（kW） | 0.none | 0.none | 15.present | 0.none | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 38.W | 0.None
0 | 0 | 15 | 0 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 38 | 0 | 0.0.15.0.19.1.37.0.0.0.0.0.0.0.0.3.38.0 | 单相表当前反向功率(kW) | 0.none | 0.none | 15.present | 0.none | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 38.W | 0.None
13 | 8 | 15 | 6 | 1 | 1 | 8 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 38 | 0 | 13.8.15.6.1.1.8.0.0.0.0.0.0.0.0.3.38.0 | 当月最大需量（kW） | 13.monthly | 8.maximum | 15.present | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 8.demand | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 38.W | 0.None
11 | 8 | 15 | 6 | 1 | 1 | 8 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 38 | 0 | 11.8.15.6.1.1.8.0.0.0.0.0.0.0.0.3.38.0 | 当日最大需量（kW） | 11.daily | 8.maximum | 15.present | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 8.demand | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 54 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 0 | 29 | 0 | 0.0.0.6.0.1.54.0.0.0.0.0.0.0.128.0.29.0 | A相表计相电压 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 54.Voltage (rms) | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 0.Not applicable or "×1" | 29.V | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 54 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 0 | 29 | 0 | 0.0.0.6.0.1.54.0.0.0.0.0.0.0.64.0.29.0 | B相表计相电压 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 54.Voltage (rms) | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 0.Not applicable or "×1" | 29.V | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 54 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 0 | 29 | 0 | 0.0.0.6.0.1.54.0.0.0.0.0.0.0.32.0.29.0 | C相表计相电压 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 54.Voltage (rms) | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 0.Not applicable or "×1" | 29.V | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 4 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 0 | 5 | 0 | 0.0.0.6.0.1.4.0.0.0.0.0.0.0.128.0.5.0 | A相表计相电流 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 4.current | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 0.Not applicable or "×1" | 5.A | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 4 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 0 | 5 | 0 | 0.0.0.6.0.1.4.0.0.0.0.0.0.0.64.0.5.0 | B相表计相电流 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 4.current | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 0.Not applicable or "×1" | 5.A | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 4 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 0 | 5 | 0 | 0.0.0.6.0.1.4.0.0.0.0.0.0.0.32.0.5.0 | C相表计相电流 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 4.current | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 0.Not applicable or "×1" | 5.A | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 54 | 0.0 | 0.0 | 0 | 0 | 0 | 132 | 0 | 29 | 0 | 0.0.0.6.0.1.54.0.0.0.0.0.0.0.132.0.29.0 | A相表计线电压 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 54.Voltage (rms) | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 132.phaseAtoB | 0.Not applicable or "×1" | 29.V | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 54 | 0.0 | 0.0 | 0 | 0 | 0 | 66 | 0 | 29 | 0 | 0.0.0.6.0.1.54.0.0.0.0.0.0.0.66.0.29.0 | B相表计线电压 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 54.Voltage (rms) | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 66.phaseBtoC | 0.Not applicable or "×1" | 29.V | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 54 | 0.0 | 0.0 | 0 | 0 | 0 | 40 | 0 | 29 | 0 | 0.0.0.6.0.1.54.0.0.0.0.0.0.0.40.0.29.0 | C相表计线电压 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 54.Voltage (rms) | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 40.phaseCtoAv | 0.Not applicable or "×1" | 29.V | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 4 | 0.0 | 0.0 | 0 | 0 | 0 | 132 | 0 | 5 | 0 | 0.0.0.6.0.1.4.0.0.0.0.0.0.0.132.0.5.0 | A相表计线电流 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 4.current | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 132.phaseAtoB | 0.Not applicable or "×1" | 5.A | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 4 | 0.0 | 0.0 | 0 | 0 | 0 | 66 | 0 | 5 | 0 | 0.0.0.6.0.1.4.0.0.0.0.0.0.0.66.0.5.0 | B相表计线电流 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 4.current | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 66.phaseBtoC | 0.Not applicable or "×1" | 5.A | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 4 | 0.0 | 0.0 | 0 | 0 | 0 | 40 | 0 | 5 | 0 | 0.0.0.6.0.1.4.0.0.0.0.0.0.0.40.0.5.0 | C相表计线电流 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 4.current | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 40.phaseCtoAv | 0.Not applicable or "×1" | 5.A | 0.None
0 | 2 | 0 | 6 | 0 | 1 | 158 | 0.0 | 0.0 | 0 | 0 | 0 | 225 | 0 | 29 | 0 | 0.2.0.6.0.1.158.0.0.0.0.0.0.0.225.0.29.0 | 三相表计平均相电压 | 0.none | 2.average | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 158.voltage | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 225.phaseABCtoN | 0.Not applicable or "×1" | 29.V | 0.None
0 | 26 | 0 | 6 | 0 | 1 | 4 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0.26.0.6.0.1.4.0.0.0.0.0.0.0.0.0.5.0 | 三相表计总电流 | 0.none | 26.sum | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 4.current | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 5.A | 0.None
0 | 26 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 3 | 38 | 0 | 0.26.0.6.1.1.37.0.0.0.0.0.0.0.224.3.38.0 | 三相表计总正向有功功率（kW） | 0.none | 26.sum | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 3.k | 38.W | 0.None
0 | 26 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 3 | 38 | 0 | 0.26.0.6.4.1.37.0.0.0.0.0.0.0.224.3.38.0 | 三相表计总净有功功率（kW） | 0.none | 26.sum | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 3.k | 38.W | 0.None
0 | 26 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 3 | 38 | 0 | 0.26.0.6.19.1.37.0.0.0.0.0.0.0.224.3.38.0 | 三相表计总反向有功功率（kvar） | 0.none | 26.sum | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 3.k | 38.W | 0.None
0 | 26 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 3 | 63 | 0 | 0.26.0.6.1.1.37.0.0.0.0.0.0.0.224.3.63.0 | 三相表计总正向无功功率（kvar） | 0.none | 26.sum | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 3.k | 63.var | 0.None
0 | 26 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 3 | 63 | 0 | 0.26.0.6.4.1.37.0.0.0.0.0.0.0.224.3.63.0 | 三相表计总净无功功率（kvar） | 0.none | 26.sum | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 3.k | 63.var | 0.None
0 | 26 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 3 | 63 | 0 | 0.26.0.6.19.1.37.0.0.0.0.0.0.0.224.3.63.0 | 三相表计总反向无功功率（kvar） | 0.none | 26.sum | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 38 | 0 | 0.0.0.6.1.1.37.0.0.0.0.0.0.0.128.3.38.0 | A相表计正向有功功率（kW） | 0.none | 0.none | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 38 | 0 | 0.0.0.6.1.1.37.0.0.0.0.0.0.0.64.3.38.0 | B相表计正向有功功率（kW） | 0.none | 0.none | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 38 | 0 | 0.0.0.6.1.1.37.0.0.0.0.0.0.0.32.3.38.0 | C相表计正向有功功率（kW） | 0.none | 0.none | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 38 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.128.3.38.0 | A相表计反向有功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 38 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.64.3.38.0 | B相表计反向有功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 38 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.32.3.38.0 | C相表计反向有功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 38 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.128.3.38.0 | A相表计净有功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 38 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.64.3.38.0 | B相表计净有功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 38 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.32.3.38.0 | C相表计净有功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 63 | 0 | 0.0.0.6.1.1.37.0.0.0.0.0.0.0.128.3.63.0 | A相表计正向无功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 63 | 0 | 0.0.0.6.1.1.37.0.0.0.0.0.0.0.64.3.63.0 | B相表计正向无功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 63 | 0 | 0.0.0.6.1.1.37.0.0.0.0.0.0.0.32.3.63.0 | C相表计正向无功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 63 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.128.3.63.0 | A相表计反向无功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 63 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.64.3.63.0 | B相表计反向无功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 63 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.32.3.63.0 | C相表计反向无功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 63 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.128.3.63.0 | A相表计净无功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 63 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.64.3.63.0 | B相表计净无功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 63 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.32.3.63.0 | C相表计净无功功率（kvar） | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 61 | 0 | 0.0.0.6.0.1.37.0.0.0.0.0.0.0.128.3.61.0 | A相表计视在功率（kVA） | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 61.VA | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 61 | 0 | 0.0.0.6.0.1.37.0.0.0.0.0.0.0.64.3.61.0 | B相表计视在功率（kVA） | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 61.VA | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 61 | 0 | 0.0.0.6.0.1.37.0.0.0.0.0.0.0.32.3.61.0 | C相表计视在功率（kVA） | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 61.VA | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 3 | 61 | 0 | 0.0.0.6.0.1.37.0.0.0.0.0.0.0.224.3.61.0 | 三相表计总视在功率（kVA） | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 3.k | 61.VA | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 38 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 0 | 65 | 0 | 0.0.0.6.0.1.38.0.0.0.0.0.0.0.224.0.65.0 | 三相表计总功率因数 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 38.powerFactor | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 0.Not applicable or "×1" | 65.Cosφ | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 38 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 0 | 65 | 0 | 0.0.0.6.0.1.38.0.0.0.0.0.0.0.128.0.65.0 | A相功率因数 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 38.powerFactor | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 0.Not applicable or "×1" | 65.Cosφ | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 38 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 0 | 65 | 0 | 0.0.0.6.0.1.38.0.0.0.0.0.0.0.64.0.65.0 | B相功率因数 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 38.powerFactor | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 0.Not applicable or "×1" | 65.Cosφ | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 38 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 0 | 65 | 0 | 0.0.0.6.0.1.38.0.0.0.0.0.0.0.32.0.65.0 | C相功率因数 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 38.powerFactor | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 0.Not applicable or "×1" | 65.Cosφ | 0.None
0 | 0 | 0 | 6 | 0 | 1 | 15 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 0 | 33 | 0 | 0.0.0.6.0.1.15.0.0.0.0.0.0.0.224.0.33.0 | 三相表计频率 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 15.frequency | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 0.Not applicable or "×1" | 33.Hz | 0.None
0 | 2 | 0 | 6 | 0 | 1 | 158 | 0.0 | 0.0 | 0 | 0 | 0 | 224 | 0 | 29 | 0 | 0.2.0.6.0.1.158.0.0.0.0.0.0.0.224.0.29.0 | 三相表计平均线电压 | 0.none | 2.average | 0.none | 6.indicating | 0.none | 1.electricity SecondaryMetered | 158.voltage | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 224.phasesABC | 0.Not applicable or "×1" | 29.V | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 38 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.128.3.38.0 |  | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 38 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.64.3.38.0 |  | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 38 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.32.3.38.0 |  | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 38 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.128.3.38.0 |  | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 38 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.64.3.38.0 |  | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 38 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.32.3.38.0 |  | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 38.W | 0.None
0 | 0 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 63 | 0 | 0.0.0.6.1.1.37.0.0.0.0.0.0.0.128.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 63 | 0 | 0.0.0.6.1.1.37.0.0.0.0.0.0.0.64.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 1 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 63 | 0 | 0.0.0.6.1.1.37.0.0.0.0.0.0.0.32.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 1.forward | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 63 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.128.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 63 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.64.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 19 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 63 | 0 | 0.0.0.6.19.1.37.0.0.0.0.0.0.0.32.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 19.reverse | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 128 | 3 | 63 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.128.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 128.phaseA | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 63 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.64.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 63 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.32.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 63.var | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
Note on R2: ZeKunZhang: Prompt参考: 根据下面输入的量测数据项各分项的配置，为这个数据项起一个名字，参考格式：【15 min递增间隔数据前向有功电能 （kW·h）】：
Note on R4: ZeKunZhang: 可用LLM Prompt参考: 根据下面输入的量测数据项各分项的配置，为这个数据项起一个名字，参考格式：【15 min递增间隔数据前向有功电能 （kW·h）】：

## ReadingTypeID储能
mRID | [15 empty] | KAIFA Project | EMS-01 | ReadingType
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | mRID | Description | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
mRID | [17 empty] | macroPeriod 宏周期 | aggregate 聚合方式 | measurePeriod 测量周期 | accumulationBehaviour 累加方式 | flowDirection 流动方向 | commodity 能源分类 | measurementKind 测量类别 | harmonic 谐波 | argument 测量序号 | TOU 分时段号 | CPP 临界峰值 | Tier 分阶梯号 | Phase 相 | multiplier 公乘因子 | uom 统一计量单位 | currency 货币计量单位
0 | 0 | 0 | 1 | 0 | 41 | 119 | 0.0 | 1.1 | 0 | 0 | 0 | 0 | 3 | 106 | 0 | 0.0.0.1.0.41.119.0.0.1.1.0.0.0.0.3.106.0 | 电池总容量(kah) | 0.none | 0.none | 0.none | 1.bulkQuantity | 0.none | 41.device | 119.batteryCarryover | 0.0.none | 1.1.n1 | 0.none | 0.none | 0.none | 0.none | 3.k | 106.Ah | 0.None
0 | 0 | 0 | 1 | 0 | 41 | 119 | 0.0 | 1.1 | 0 | 0 | 0 | 0 | 3 | 72 | 0 | 0.0.0.1.0.41.119.0.0.1.1.0.0.0.0.3.72.0 | 电池总容量(kwh) | 0.none | 0.none | 0.none | 1.bulkQuantity | 0.none | 41.device | 119.batteryCarryover | 0.0.none | 1.1.n1 | 0.none | 0.none | 0.none | 0.none | 3.k | 72.W·h | 0.None
0 | 0 | 0 | 0 | 20 | 1 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.0.0.20.1.0.0.0.0.0.0.0.0.0.0.109.0 | PCS充放电状态 | 0.none | 0.none | 0.none | 0.none | 20.total | 1.electricity SecondaryMetered | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
0 | 0 | 0 | 0 | 0 | 41 | 118 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.0.0.0.41.118.0.0.0.0.0.0.0.0.0.109.0 | 系统故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 41.device | 118.alarm | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
0 | 0 | 0 | 0 | 0 | 3 | 139 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.0.0.0.3.139.0.0.0.0.0.0.0.0.0.109.0 | 在线状态 | 0.none | 0.none | 0.none | 0.none | 0.none | 3.communication | 139.programmed | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
0 | 0 | 15 | 1 | 0 | 41 | 901 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –2 | 801 | 0 | 0.0.15.1.0.41.901.0.0.0.0.0.0.0.0.–2 .801.0 | SOC | 0.none | 0.none | 15.present | 1.bulkQuantity | 0.none | 41.device | SOC | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –2 .c | % | 0.None
0 | 0 | 15 | 1 | 0 | 41 | 902 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –2 | 801 | 0 | 0.0.15.1.0.41.902.0.0.0.0.0.0.0.0.–2 .801.0 | SOH | 0.none | 0.none | 15.present | 1.bulkQuantity | 0.none | 41.device | SOH | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –2 .c | % | 0.None
0 | 0 | 15 | 0 | 0 | 41 | 139 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.15.0.0.41.139.0.0.0.0.0.0.0.0.0.109.0 | 电池运行状态 | 0.none | 0.none | 15.present | 0.none | 0.none | 41.device | 139.programmed | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
0 | 0 | 15 | 0 | 1 | 41 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0.0.15.0.1.41.0.0.0.0.0.0.0.0.0.0.30.0 | 电池绝缘电阻R+ | 0.none | 0.none | 15.present | 0.none | 1.forward | 41.device | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 30.Ohm (V/A) | 0.None
0 | 0 | 15 | 0 | 19 | 41 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0.0.15.0.19.41.0.0.0.0.0.0.0.0.0.0.30.0 | 电池绝缘电阻R- | 0.none | 0.none | 15.present | 0.none | 19.reverse | 41.device | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 30.Ohm (V/A) | 0.None
0 | 26 | 15 | 1 | 0 | 41 | 158 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0.26.15.1.0.41.158.0.0.0.0.0.0.0.0.0.29.0 | 电池总电压 | 0.none | 26.sum | 15.present | 1.bulkQuantity | 0.none | 41.device | 158.voltage | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 29.V | 0.None
0 | 26 | 15 | 1 | 1 | 41 | 3 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0.26.15.1.1.41.3.0.0.0.0.0.0.0.0.0.29.0 | 电池总电流 | 0.none | 26.sum | 15.present | 1.bulkQuantity | 1.forward | 41.device | 3.currency | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 29.V | 0.None
0 | 9 | 15 | 0 | 0 | 41 | 46 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0.9.15.0.0.41.46.0.0.0.0.0.0.0.0.0.23.0 | 电池最低温度 | 0.none | 9.minimum | 15.present | 0.none | 0.none | 41.device | 46.temperature | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 23.degrees Celsius | 0.None
0 | 8 | 15 | 0 | 0 | 41 | 46 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0.8.15.0.0.41.46.0.0.0.0.0.0.0.0.0.23.0 | 电池最高温度 | 0.none | 8.maximum | 15.present | 0.none | 0.none | 41.device | 46.temperature | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 23.degrees Celsius | 0.None
0 | 2 | 15 | 0 | 0 | 41 | 46 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0.2.15.0.0.41.46.0.0.0.0.0.0.0.0.0.23.0 | 电池平均温度 | 0.none | 2.average | 15.present | 0.none | 0.none | 41.device | 46.temperature | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 23.degrees Celsius | 0.None
0 | 2 | 15 | 0 | 0 | 41 | 158 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –3 | 29 | 0 | 0.2.15.0.0.41.158.0.0.0.0.0.0.0.0.–3 .29.0 | 单体平均电压 单位mV | 0.none | 2.average | 15.present | 0.none | 0.none | 41.device | 158.voltage | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –3 .m | 29.V | 0.None
0 | 9 | 15 | 0 | 0 | 41 | 158 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –3 | 29 | 0 | 0.9.15.0.0.41.158.0.0.0.0.0.0.0.0.–3 .29.0 | 最低单体电压 单位mV | 0.none | 9.minimum | 15.present | 0.none | 0.none | 41.device | 158.voltage | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –3 .m | 29.V | 0.None
0 | 8 | 15 | 0 | 0 | 41 | 158 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –3 | 29 | 0 | 0.8.15.0.0.41.158.0.0.0.0.0.0.0.0.–3 .29.0 | 最高单体电压 单位mV | 0.none | 8.maximum | 15.present | 0.none | 0.none | 41.device | 158.voltage | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –3 .m | 29.V | 0.None
0 | 0 | 15 | 0 | 0 | 41 | 46 | 0.0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0.0.15.0.0.41.46.0.0.1.1.0.0.0.0.0.23.0 | 电池温度 | 0.none | 0.none | 15.present | 0.none | 0.none | 41.device | 46.temperature | 0.0.none | 1.1.n1 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 23.degrees Celsius | 0.None
0 | 0 | 0 | 0 | 0 | 2 | 11 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.0.0.0.2.11.0.0.0.0.0.0.0.0.0.109.0 | 并/离网状态 | 0.none | 0.none | 0.none | 0.none | 0.none | 2.electricity PrimaryMetered | 11.energization | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
0 | 0 | 0 | 0 | 0 | 2 | 903 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –2 | 801 | 0 | 0.0.0.0.0.2.903.0.0.0.0.0.0.0.0.–2 .801.0 | PCS效率 | 0.none | 0.none | 0.none | 0.none | 0.none | 2.electricity PrimaryMetered | efficiency | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –2 .c | % | 0.None
0 | 0 | 0 | 0 | 0 | #N/A | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 38 | 0 | #N/A | 直流电池功率 | 0.none | 0.none | 0.none | 0.none | 0.none | 901.1.electricity DirectMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 38.W | 0.None
0 | 0 | 0 | 0 | 0 | 2 | 904 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.0.0.0.2.904.0.0.0.0.0.0.0.0.0.109.0 | 就地/远方状态 | 0.none | 0.none | 0.none | 0.none | 0.none | 2.electricity PrimaryMetered | ControlMode | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
0 | 4 | 2 | 10 | 4 | 41 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 38 | 0 | 0.4.2.10.4.41.37.0.0.0.0.0.0.0.0.3.38.0 | 本地EMS计划执行曲线 | 0.none | 4.excess | 2.fifteenMinute | 10.timeDelay | 4.net | 41.device | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 38.W | 0.None
0 | 0 | 0 | 0 | 0 | 41 | 11 | 0.0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.0.0.0.41.11.0.0.1.1.0.0.0.0.0.109.0 | 负荷跟踪使能 | 0.none | 0.none | 0.none | 0.none | 0.none | 41.device | 11.energization | 0.0.none | 1.1.n1 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
0 | 0 | 0 | 0 | 19 | 41 | 11 | 0.0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.0.0.19.41.11.0.0.2.1.0.0.0.0.0.109.0 | 逆流跟踪使能 | 0.none | 0.none | 0.none | 0.none | 19.reverse | 41.device | 11.energization | 0.0.none | 2.1.n2 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
0 | 0 | 0 | 0 | 0 | 41 | 11 | 0.0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.0.0.0.41.11.0.0.3.1.0.0.0.0.0.109.0 | 变压器需量使能 | 0.none | 0.none | 0.none | 0.none | 0.none | 41.device | 11.energization | 0.0.none | 3.1.n3 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
0 | 0 | 0 | 0 | 0 | 41 | 11 | 0.0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0.0.0.0.0.41.11.0.0.4.1.0.0.0.0.0.109.0 | DOD防护使能 | 0.none | 0.none | 0.none | 0.none | 0.none | 41.device | 11.energization | 0.0.none | 4.1.n4 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 109.State | 0.None
13 | 0 | 0 | 0 | 0 | 41 | 121 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 801 | 0 | 13.0.0.0.0.41.121.0.0.0.0.0.0.0.0.0.801.0 | 需量控制系数 | 13.monthly | 0.none | 0.none | 0.none | 0.none | 41.device | 121.demandLimit | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | % | 0.None
0 | 8 | 15 | 1 | 1 | 41 | 901 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –2 | 801 | 0 | 0.8.15.1.1.41.901.0.0.0.0.0.0.0.0.–2 .801.0 | 最大充电SOC | 0.none | 8.maximum | 15.present | 1.bulkQuantity | 1.forward | 41.device | SOC | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –2 .c | % | 0.None
0 | 9 | 15 | 1 | 19 | 41 | 901 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –2 | 801 | 0 | 0.9.15.1.19.41.901.0.0.0.0.0.0.0.0.–2 .801.0 | 最小放电SOC | 0.none | 9.minimum | 15.present | 1.bulkQuantity | 19.reverse | 41.device | SOC | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –2 .c | % | 0.None
0 | 0 | 0 | 0 | 19 | 41 | 183 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 3 | 38 | 0 | 0.0.0.0.19.41.183.0.0.0.0.0.0.0.0.3.38.0 | 防逆流余量 | 0.none | 0.none | 0.none | 0.none | 19.reverse | 41.device | 183.batteryChargeMoved | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 3.k | 38.W | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 | 调整间隔（秒） | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
Note on R2: ZeKunZhang: Prompt参考: 根据下面输入的量测数据项各分项的配置，为这个数据项起一个名字，参考格式：【15 min递增间隔数据前向有功电能 （kW·h）】：

## ReadingTypeID告警
mRID | [15 empty] | KAIFA Project | EMS-01 | ReadingType
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | mRID | Description | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
mRID | [17 empty] | macroPeriod 宏周期 | aggregate 聚合方式 | measurePeriod 测量周期 | accumulationBehaviour 累加方式 | flowDirection 流动方向 | commodity 能源分类 | measurementKind 测量类别 | harmonic 谐波 | argument 测量序号 | TOU 分时段号 | CPP 临界峰值 | Tier 分阶梯号 | Phase 相 | multiplier 公乘因子 | uom 统一计量单位 | currency 货币计量单位
0 | 0 | 15 | 0 | 0 | 41 | 118 | 0.0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.15.0.0.41.118.0.0.1.1.0.0.0.0.0.0.0 | 组端过压1级报警 | 0.none | 0.none | 15.present | 0.none | 0.none | 41.device | 118.alarm | 0.0.none | 0.1.n0 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.2.1.0.0.0.0.0.0.0 | 组端过压2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.3.1.0.0.0.0.0.0.0 | 组端过压3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.4.1.0.0.0.0.0.0.0 | 组端欠压1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.5.1.0.0.0.0.0.0.0 | 组端欠压2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.6.1.0.0.0.0.0.0.0 | 组端欠压3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.7.1.0.0.0.0.0.0.0 | 组端放电过流1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.8.1.0.0.0.0.0.0.0 | 组端放电过流2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.9.1.0.0.0.0.0.0.0 | 组端放电过流3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.10.1.0.0.0.0.0.0.0 | 组端充电过流1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.11.1.0.0.0.0.0.0.0 | 组端充电过流2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.12.1.0.0.0.0.0.0.0 | 组端充电过流3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.13.1.0.0.0.0.0.0.0 | 组端绝缘1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.14.1.0.0.0.0.0.0.0 | 组端绝缘2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.15.1.0.0.0.0.0.0.0 | 组端绝缘3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.16.1.0.0.0.0.0.0.0 | 单体电池充电过温1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.17.1.0.0.0.0.0.0.0 | 单体电池充电过温2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.18.1.0.0.0.0.0.0.0 | 单体电池充电过温3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.19.1.0.0.0.0.0.0.0 | 单体电池充电欠温1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.20.1.0.0.0.0.0.0.0 | 单体电池充电欠温2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.21.1.0.0.0.0.0.0.0 | 单体电池充电欠温3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.22.1.0.0.0.0.0.0.0 | 单体电压过压1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.23.1.0.0.0.0.0.0.0 | 单体电压过压2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.24.1.0.0.0.0.0.0.0 | 单体电压过压3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.25.1.0.0.0.0.0.0.0 | 单体电压欠压1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.26.1.0.0.0.0.0.0.0 | 单体电压欠压2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.27.1.0.0.0.0.0.0.0 | 单体电压欠压3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.28.1.0.0.0.0.0.0.0 | 单体压差过高1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.29.1.0.0.0.0.0.0.0 | 单体压差过高2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.30.1.0.0.0.0.0.0.0 | 单体压差过高3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.31.1.0.0.0.0.0.0.0 | 单体温差过高1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.32.1.0.0.0.0.0.0.0 | 单体温差过高2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.33.1.0.0.0.0.0.0.0 | 单体温差过高3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.34.1.0.0.0.0.0.0.0 | SOC过低1级告警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.35.1.0.0.0.0.0.0.0 | SOC过低2级告警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.36.1.0.0.0.0.0.0.0 | SOC过低3级告警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.37.1.0.0.0.0.0.0.0 | 动力插箱温度过高1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.38.1.0.0.0.0.0.0.0 | 动力插箱温度过高2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.39.1.0.0.0.0.0.0.0 | 动力插箱温度过高3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.40.1.0.0.0.0.0.0.0 | 电池模组过压1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.41.1.0.0.0.0.0.0.0 | 电池模组过压2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.42.1.0.0.0.0.0.0.0 | 电池模组过压3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.43.1.0.0.0.0.0.0.0 | 电池模组欠压1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.44.1.0.0.0.0.0.0.0 | 电池模组欠压2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.45.1.0.0.0.0.0.0.0 | 电池模组欠压3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.46.1.0.0.0.0.0.0.0 | DI1故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.47.1.0.0.0.0.0.0.0 | DI2故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.48.1.0.0.0.0.0.0.0 | DI3故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.49.1.0.0.0.0.0.0.0 | DI4故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.50.1.0.0.0.0.0.0.0 | DI5故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.51.1.0.0.0.0.0.0.0 | DI6故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.52.1.0.0.0.0.0.0.0 | DI7故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.53.1.0.0.0.0.0.0.0 | DI8故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.54.1.0.0.0.0.0.0.0 | 内网通讯失联 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.55.1.0.0.0.0.0.0.0 | 单体电压采集异常 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.56.1.0.0.0.0.0.0.0 | 单体温度采集异常 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.57.1.0.0.0.0.0.0.0 | 显控检测故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.58.1.0.0.0.0.0.0.0 | 簇间压差大 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.59.1.0.0.0.0.0.0.0 | 簇间跳机故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.60.1.0.0.0.0.0.0.0 | 电池极限故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.61.1.0.0.0.0.0.0.0 | 项目软件版本参数不一致 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.62.1.0.0.0.0.0.0.0 | PCS通讯故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.63.1.0.0.0.0.0.0.0 | PC强控调试模式 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.64.1.0.0.0.0.0.0.0 | CAN霍尔传感器故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.65.1.0.0.0.0.0.0.0 | CAN霍尔传感器通讯故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.66.1.0.0.0.0.0.0.0 | 硬件自检异常 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.67.1.0.0.0.0.0.0.0 | 单体电压线束故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.68.1.0.0.0.0.0.0.0 | 均衡故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.69.1.0.0.0.0.0.0.0 | EMS通讯故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.70.1.0.0.0.0.0.0.0 | 与三级BMS通讯故障 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.71.1.0.0.0.0.0.0.0 | 单体电池放电过温1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.72.1.0.0.0.0.0.0.0 | 单体电池放电过温2级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.73.1.0.0.0.0.0.0.0 | 单体电池放电过温3级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.15.0.0.41.118.0.0.74.1.0.0.0.0.0.0.0 | 单体电池放电欠温1级报警 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
[16 empty] | 0.0.15.0.0.41.118.0.0.75.1.0.0.0.0.0.0.0 | 单体电池放电欠温2级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.76.1.0.0.0.0.0.0.0 | 单体电池放电欠温3级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.77.1.0.0.0.0.0.0.0 | SOC过高1级告警
[16 empty] | 0.0.15.0.0.41.118.0.0.78.1.0.0.0.0.0.0.0 | SOC过高2级告警
[16 empty] | 0.0.15.0.0.41.118.0.0.79.1.0.0.0.0.0.0.0 | SOC过高3级告警
[16 empty] | 0.0.15.0.0.41.118.0.0.80.1.0.0.0.0.0.0.0 | 温升快报警1级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.81.1.0.0.0.0.0.0.0 | 温升快报警2级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.82.1.0.0.0.0.0.0.0 | 温升快报警3级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.83.1.0.0.0.0.0.0.0 | 预充失败
[16 empty] | 0.0.15.0.0.41.118.0.0.84.1.0.0.0.0.0.0.0 | 单体温度采集故障一级告警
[16 empty] | 0.0.15.0.0.41.118.0.0.85.1.0.0.0.0.0.0.0 | 单体温度采集故障二级告警
[16 empty] | 0.0.15.0.0.41.118.0.0.86.1.0.0.0.0.0.0.0 | 从控内温差大1 级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.87.1.0.0.0.0.0.0.0 | 从控内温差大2级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.88.1.0.0.0.0.0.0.0 | 从控内温差大3级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.89.1.0.0.0.0.0.0.0 | 从控内压差大1级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.90.1.0.0.0.0.0.0.0 | 从控内压差大2级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.91.1.0.0.0.0.0.0.0 | 从控内压差大3级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.92.1.0.0.0.0.0.0.0 | 从控总压压差大1级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.93.1.0.0.0.0.0.0.0 | 从控总压压差大2级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.94.1.0.0.0.0.0.0.0 | 从控总压压差大3级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.95.1.0.0.0.0.0.0.0 | DBC使能开启
[16 empty] | 0.0.15.0.0.41.118.0.0.96.1.0.0.0.0.0.0.0 | 菊花链单环故障
[16 empty] | 0.0.15.0.0.41.118.0.0.97.1.0.0.0.0.0.0.0 | 单体电压采集芯片故障
[16 empty] | 0.0.15.0.0.41.118.0.0.98.1.0.0.0.0.0.0.0 | 极柱温度采集故障1级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.99.1.0.0.0.0.0.0.0 | 极柱温度采集故障2级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.100.1.0.0.0.0.0.0.0 | 极柱温度采集故障3级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.101.1.0.0.0.0.0.0.0 | 主控供电过压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.102.1.0.0.0.0.0.0.0 | 主控供电欠压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.103.1.0.0.0.0.0.0.0 | 主控程序运行故障
[16 empty] | 0.0.15.0.0.41.118.0.0.104.1.0.0.0.0.0.0.0 | 从控程序运行故障
[16 empty] | 0.0.15.0.0.41.118.0.0.105.1.0.0.0.0.0.0.0 | 主控EEPROM故障
[16 empty] | 0.0.15.0.0.41.118.0.0.106.1.0.0.0.0.0.0.0 | 主控Flash故障
[16 empty] | 0.0.15.0.0.41.118.0.0.107.1.0.0.0.0.0.0.0 | 从控EEPROM故障
[16 empty] | 0.0.15.0.0.41.118.0.0.108.1.0.0.0.0.0.0.0 | 单体电压不刷新
[16 empty] | 0.0.15.0.0.41.118.0.0.109.1.0.0.0.0.0.0.0 | AFE供电故障
[16 empty] | 0.0.15.0.0.41.118.0.0.110.1.0.0.0.0.0.0.0 | 主控12V输出电压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.111.1.0.0.0.0.0.0.0 | 主控RTC故障
[16 empty] | 0.0.15.0.0.41.118.0.0.112.1.0.0.0.0.0.0.0 | CAB500故障
[16 empty] | 0.0.15.0.0.41.118.0.0.113.1.0.0.0.0.0.0.0 | 模拟量霍尔故障
[16 empty] | 0.0.15.0.0.41.118.0.0.114.1.0.0.0.0.0.0.0 | 电池总压检测电路故障
[16 empty] | 0.0.15.0.0.41.118.0.0.115.1.0.0.0.0.0.0.0 | 电池负载侧电压检测电路故障
[16 empty] | 0.0.15.0.0.41.118.0.0.116.1.0.0.0.0.0.0.0 | 绝缘电路故障
[16 empty] | 0.0.15.0.0.41.118.0.0.117.1.0.0.0.0.0.0.0 | SOC跳变故障
[16 empty] | 0.0.15.0.0.41.118.0.0.118.1.0.0.0.0.0.0.0 | 电池簇充放电回路连接铜排虚接
[16 empty] | 0.0.15.0.0.41.118.0.0.119.1.0.0.0.0.0.0.0 | 单体热失控预警
[16 empty] | 0.0.15.0.0.41.118.0.0.120.1.0.0.0.0.0.0.0 | 极柱温差大1级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.121.1.0.0.0.0.0.0.0 | 极柱温差大2级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.122.1.0.0.0.0.0.0.0 | 极柱温差大3级报警
[16 empty] | 0.0.15.0.0.41.118.0.0.123.1.0.0.0.0.0.0.0 | 簇安全阀异常告警
[16 empty] | 0.0.15.0.0.41.118.0.0.124.1.0.0.0.0.0.0.0 | 系统告警状态
[16 empty] | 0.0.15.0.0.41.118.0.0.125.1.0.0.0.0.0.0.0 | 系统故障
[16 empty] | 0.0.15.0.0.41.118.0.0.126.1.0.0.0.0.0.0.0 | 硬件故障字1
[16 empty] | 0.0.15.0.0.41.118.0.0.127.1.0.0.0.0.0.0.0 | EPO故障
[16 empty] | 0.0.15.0.0.41.118.0.0.128.1.0.0.0.0.0.0.0 | IGBT硬件过流
[16 empty] | 0.0.15.0.0.41.118.0.0.129.1.0.0.0.0.0.0.0 | 母线硬件过压
[16 empty] | 0.0.15.0.0.41.118.0.0.130.1.0.0.0.0.0.0.0 | 功率模块逐波限流
[16 empty] | 0.0.15.0.0.41.118.0.0.131.1.0.0.0.0.0.0.0 | 平衡模块硬件过流
[16 empty] | 0.0.15.0.0.41.118.0.0.132.1.0.0.0.0.0.0.0 | 硬件故障字2
[16 empty] | 0.0.15.0.0.41.118.0.0.133.1.0.0.0.0.0.0.0 | 24V电源故障
[16 empty] | 0.0.15.0.0.41.118.0.0.134.1.0.0.0.0.0.0.0 | 风扇故障
[16 empty] | 0.0.15.0.0.41.118.0.0.135.1.0.0.0.0.0.0.0 | 连接故障
[16 empty] | 0.0.15.0.0.41.118.0.0.136.1.0.0.0.0.0.0.0 | 外部输入干接点 3 故障
[16 empty] | 0.0.15.0.0.41.118.0.0.137.1.0.0.0.0.0.0.0 | 电感过温
[16 empty] | 0.0.15.0.0.41.118.0.0.138.1.0.0.0.0.0.0.0 | 功率模块过温
[16 empty] | 0.0.15.0.0.41.118.0.0.139.1.0.0.0.0.0.0.0 | 平衡模块过温
[16 empty] | 0.0.15.0.0.41.118.0.0.140.1.0.0.0.0.0.0.0 | 15V电源故障
[16 empty] | 0.0.15.0.0.41.118.0.0.141.1.0.0.0.0.0.0.0 | 系统火警故障
[16 empty] | 0.0.15.0.0.41.118.0.0.142.1.0.0.0.0.0.0.0 | 外部输入干接点 1 故障；
[16 empty] | 0.0.15.0.0.41.118.0.0.143.1.0.0.0.0.0.0.0 | 外部输入干接点 2 故障
[16 empty] | 0.0.15.0.0.41.118.0.0.144.1.0.0.0.0.0.0.0 | 环境温度过温故障；
[16 empty] | 0.0.15.0.0.41.118.0.0.145.1.0.0.0.0.0.0.0 | 干接点过温故障
[16 empty] | 0.0.15.0.0.41.118.0.0.146.1.0.0.0.0.0.0.0 | 电网故障字
[16 empty] | 0.0.15.0.0.41.118.0.0.147.1.0.0.0.0.0.0.0 | A相过压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.148.1.0.0.0.0.0.0.0 | B相过压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.149.1.0.0.0.0.0.0.0 | C相过压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.150.1.0.0.0.0.0.0.0 | A相欠压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.151.1.0.0.0.0.0.0.0 | B相欠压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.152.1.0.0.0.0.0.0.0 | C相欠压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.153.1.0.0.0.0.0.0.0 | 电网过频
[16 empty] | 0.0.15.0.0.41.118.0.0.154.1.0.0.0.0.0.0.0 | 电网欠频
[16 empty] | 0.0.15.0.0.41.118.0.0.155.1.0.0.0.0.0.0.0 | 电网相序错误
[16 empty] | 0.0.15.0.0.41.118.0.0.156.1.0.0.0.0.0.0.0 | A相软件过流
[16 empty] | 0.0.15.0.0.41.118.0.0.157.1.0.0.0.0.0.0.0 | B相软件过流
[16 empty] | 0.0.15.0.0.41.118.0.0.158.1.0.0.0.0.0.0.0 | C相软件过流
[16 empty] | 0.0.15.0.0.41.118.0.0.159.1.0.0.0.0.0.0.0 | 电网电压不平衡
[16 empty] | 0.0.15.0.0.41.118.0.0.160.1.0.0.0.0.0.0.0 | 电网电流不平衡
[16 empty] | 0.0.15.0.0.41.118.0.0.161.1.0.0.0.0.0.0.0 | 电网缺相
[16 empty] | 0.0.15.0.0.41.118.0.0.162.1.0.0.0.0.0.0.0 | N线过流
[16 empty] | 0.0.15.0.0.41.118.0.0.163.1.0.0.0.0.0.0.0 | 母线故障字
[16 empty] | 0.0.15.0.0.41.118.0.0.164.1.0.0.0.0.0.0.0 | 预充母线过压
[16 empty] | 0.0.15.0.0.41.118.0.0.165.1.0.0.0.0.0.0.0 | 预充母线欠压
[16 empty] | 0.0.15.0.0.41.118.0.0.166.1.0.0.0.0.0.0.0 | 不控整流母线过压
[16 empty] | 0.0.15.0.0.41.118.0.0.167.1.0.0.0.0.0.0.0 | 不控整流母线欠压
[16 empty] | 0.0.15.0.0.41.118.0.0.168.1.0.0.0.0.0.0.0 | 运行母线过压
[16 empty] | 0.0.15.0.0.41.118.0.0.169.1.0.0.0.0.0.0.0 | 运行母线欠压
[16 empty] | 0.0.15.0.0.41.118.0.0.170.1.0.0.0.0.0.0.0 | 正负母线不平衡
[16 empty] | 0.0.15.0.0.41.118.0.0.171.1.0.0.0.0.0.0.0 | 电池欠压
[16 empty] | 0.0.15.0.0.41.118.0.0.172.1.0.0.0.0.0.0.0 | 电流模式母线欠压
[16 empty] | 0.0.15.0.0.41.118.0.0.173.1.0.0.0.0.0.0.0 | 电池过压
[16 empty] | 0.0.15.0.0.41.118.0.0.174.1.0.0.0.0.0.0.0 | 直流预充电过流
[16 empty] | 0.0.15.0.0.41.118.0.0.175.1.0.0.0.0.0.0.0 | 直流过流
[16 empty] | 0.0.15.0.0.41.118.0.0.176.1.0.0.0.0.0.0.0 | 平衡模块软件过流
[16 empty] | 0.0.15.0.0.41.118.0.0.177.1.0.0.0.0.0.0.0 | 电池反接
[16 empty] | 0.0.15.0.0.41.118.0.0.178.1.0.0.0.0.0.0.0 | 交流电容故障字
[16 empty] | 0.0.15.0.0.41.118.0.0.179.1.0.0.0.0.0.0.0 | 预充电超时
[16 empty] | 0.0.15.0.0.41.118.0.0.180.1.0.0.0.0.0.0.0 | 预充电A相过流
[16 empty] | 0.0.15.0.0.41.118.0.0.181.1.0.0.0.0.0.0.0 | 预充电B相过流
[16 empty] | 0.0.15.0.0.41.118.0.0.182.1.0.0.0.0.0.0.0 | 预充电C相过流
[16 empty] | 0.0.15.0.0.41.118.0.0.183.1.0.0.0.0.0.0.0 | 漏电流故障
[16 empty] | 0.0.15.0.0.41.118.0.0.184.1.0.0.0.0.0.0.0 | 系统故障字
[16 empty] | 0.0.15.0.0.41.118.0.0.185.1.0.0.0.0.0.0.0 | 控制板RAM故障
[16 empty] | 0.0.15.0.0.41.118.0.0.186.1.0.0.0.0.0.0.0 | 控制板EEPROM故障
[16 empty] | 0.0.15.0.0.41.118.0.0.187.1.0.0.0.0.0.0.0 | AD采样零漂故障
[16 empty] | 0.0.15.0.0.41.118.0.0.188.1.0.0.0.0.0.0.0 | 控制板后台通讯协议故障
[16 empty] | 0.0.15.0.0.41.118.0.0.189.1.0.0.0.0.0.0.0 | 控制板CAN通讯协议故障
[16 empty] | 0.0.15.0.0.41.118.0.0.190.1.0.0.0.0.0.0.0 | 控制板CPLD通讯协议故障
[16 empty] | 0.0.15.0.0.41.118.0.0.191.1.0.0.0.0.0.0.0 | 控制板DataLog数据故障
[16 empty] | 0.0.15.0.0.41.118.0.0.192.1.0.0.0.0.0.0.0 | 绝缘检测故障
[16 empty] | 0.0.15.0.0.41.118.0.0.193.1.0.0.0.0.0.0.0 | 软件固件不匹配故障
[16 empty] | 0.0.15.0.0.41.118.0.0.194.1.0.0.0.0.0.0.0 | BMS电池系统故障
[16 empty] | 0.0.15.0.0.41.118.0.0.195.1.0.0.0.0.0.0.0 | STS通信故障
[16 empty] | 0.0.15.0.0.41.118.0.0.196.1.0.0.0.0.0.0.0 | BMS通讯故障
[16 empty] | 0.0.15.0.0.41.118.0.0.197.1.0.0.0.0.0.0.0 | 从模块CAN通信故障
[16 empty] | 0.0.15.0.0.41.118.0.0.198.1.0.0.0.0.0.0.0 | EMS通信故障
[16 empty] | 0.0.15.0.0.41.118.0.0.199.1.0.0.0.0.0.0.0 | 开关故障字
[16 empty] | 0.0.15.0.0.41.118.0.0.200.1.0.0.0.0.0.0.0 | 预充电继电器闭合失败
[16 empty] | 0.0.15.0.0.41.118.0.0.201.1.0.0.0.0.0.0.0 | 预充电继电器断开失败
[16 empty] | 0.0.15.0.0.41.118.0.0.202.1.0.0.0.0.0.0.0 | 预充电继电器闭合状态错误
[16 empty] | 0.0.15.0.0.41.118.0.0.203.1.0.0.0.0.0.0.0 | 预充电继电器断开状态错误
[16 empty] | 0.0.15.0.0.41.118.0.0.204.1.0.0.0.0.0.0.0 | 主继电器闭合失败
[16 empty] | 0.0.15.0.0.41.118.0.0.205.1.0.0.0.0.0.0.0 | 主继电器断开失败
[16 empty] | 0.0.15.0.0.41.118.0.0.206.1.0.0.0.0.0.0.0 | 主继电器闭合状态错误
[16 empty] | 0.0.15.0.0.41.118.0.0.207.1.0.0.0.0.0.0.0 | 主继电器断开状态错误
[16 empty] | 0.0.15.0.0.41.118.0.0.208.1.0.0.0.0.0.0.0 | 交流主继电器粘连故障
[16 empty] | 0.0.15.0.0.41.118.0.0.209.1.0.0.0.0.0.0.0 | 直流继电器开路故障
[16 empty] | 0.0.15.0.0.41.118.0.0.210.1.0.0.0.0.0.0.0 | 交流主继电器开路故障
[16 empty] | 0.0.15.0.0.41.118.0.0.211.1.0.0.0.0.0.0.0 | 其他故障字
[16 empty] | 0.0.15.0.0.41.118.0.0.212.1.0.0.0.0.0.0.0 | 逆变电压A相过压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.213.1.0.0.0.0.0.0.0 | 逆变电压B相过压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.214.1.0.0.0.0.0.0.0 | 逆变电压C相过压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.215.1.0.0.0.0.0.0.0 | 电网孤岛故障
[16 empty] | 0.0.15.0.0.41.118.0.0.216.1.0.0.0.0.0.0.0 | 系统谐振故障
[16 empty] | 0.0.15.0.0.41.118.0.0.217.1.0.0.0.0.0.0.0 | 软件过压过流
[16 empty] | 0.0.15.0.0.41.118.0.0.218.1.0.0.0.0.0.0.0 | 高电压穿越超时故障
[16 empty] | 0.0.15.0.0.41.118.0.0.219.1.0.0.0.0.0.0.0 | 逆变电压A相欠压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.220.1.0.0.0.0.0.0.0 | 逆变电压B相欠压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.221.1.0.0.0.0.0.0.0 | 逆变电压C相欠压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.222.1.0.0.0.0.0.0.0 | 离网无同步信号故障
[16 empty] | 0.0.15.0.0.41.118.0.0.223.1.0.0.0.0.0.0.0 | 离网短路故障
[16 empty] | 0.0.15.0.0.41.118.0.0.224.1.0.0.0.0.0.0.0 | 低电压穿越超时故障
[16 empty] | 0.0.15.0.0.41.118.0.0.225.1.0.0.0.0.0.0.0 | 故障状态1
[16 empty] | 0.0.15.0.0.41.118.0.0.226.1.0.0.0.0.0.0.0 | 供水泵故障
[16 empty] | 0.0.15.0.0.41.118.0.0.227.1.0.0.0.0.0.0.0 | 泵空转保护
[16 empty] | 0.0.15.0.0.41.118.0.0.228.1.0.0.0.0.0.0.0 | 泵堵转保护
[16 empty] | 0.0.15.0.0.41.118.0.0.229.1.0.0.0.0.0.0.0 | 泵过流故障
[16 empty] | 0.0.15.0.0.41.118.0.0.230.1.0.0.0.0.0.0.0 | 泵欠压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.231.1.0.0.0.0.0.0.0 | 泵过压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.232.1.0.0.0.0.0.0.0 | 预充故障
[16 empty] | 0.0.15.0.0.41.118.0.0.233.1.0.0.0.0.0.0.0 | 泵驱动过热保护故障
[16 empty] | 0.0.15.0.0.41.118.0.0.234.1.0.0.0.0.0.0.0 | 供水压力传感器故障
[16 empty] | 0.0.15.0.0.41.118.0.0.235.1.0.0.0.0.0.0.0 | 主板IIC故障
[16 empty] | 0.0.15.0.0.41.118.0.0.236.1.0.0.0.0.0.0.0 | 回水压力低故障
[16 empty] | 0.0.15.0.0.41.118.0.0.237.1.0.0.0.0.0.0.0 | 供水压力过高
[16 empty] | 0.0.15.0.0.41.118.0.0.238.1.0.0.0.0.0.0.0 | 电压过高
[16 empty] | 0.0.15.0.0.41.118.0.0.239.1.0.0.0.0.0.0.0 | 电压过低
[16 empty] | 0.0.15.0.0.41.118.0.0.240.1.0.0.0.0.0.0.0 | 故障状态2
[16 empty] | 0.0.15.0.0.41.118.0.0.241.1.0.0.0.0.0.0.0 | 系统低压
[16 empty] | 0.0.15.0.0.41.118.0.0.242.1.0.0.0.0.0.0.0 | 电加热保护
[16 empty] | 0.0.15.0.0.41.118.0.0.243.1.0.0.0.0.0.0.0 | 风机过载
[16 empty] | 0.0.15.0.0.41.118.0.0.244.1.0.0.0.0.0.0.0 | 系统高压故障
[16 empty] | 0.0.15.0.0.41.118.0.0.245.1.0.0.0.0.0.0.0 | 蒸发进口探头故障
[16 empty] | 0.0.15.0.0.41.118.0.0.246.1.0.0.0.0.0.0.0 | 蒸发出口探头故障
[16 empty] | 0.0.15.0.0.41.118.0.0.247.1.0.0.0.0.0.0.0 | 系统高压报警锁定
[16 empty] | 0.0.15.0.0.41.118.0.0.248.1.0.0.0.0.0.0.0 | 排气压力传感器故障
[16 empty] | 0.0.15.0.0.41.118.0.0.249.1.0.0.0.0.0.0.0 | 压缩机变频器通讯故障
[16 empty] | 0.0.15.0.0.41.118.0.0.250.1.0.0.0.0.0.0.0 | 故障状态3
[16 empty] | 0.0.15.0.0.41.118.0.0.251.1.0.0.0.0.0.0.0 | 液温探头故障
[16 empty] | 0.0.15.0.0.41.118.0.0.252.1.0.0.0.0.0.0.0 | 回液探头故障
[16 empty] | 0.0.15.0.0.41.118.0.0.253.1.0.0.0.0.0.0.0 | 环境探头故障
[16 empty] | 0.0.15.0.0.41.118.0.0.254.1.0.0.0.0.0.0.0 | 液温过高
[16 empty] | 0.0.15.0.0.41.118.0.0.255.1.0.0.0.0.0.0.0 | 回水压力传感器故障
[16 empty] | 0.0.15.0.0.41.118.0.0.256.1.0.0.0.0.0.0.0 | 屏幕与主板通讯超时
[16 empty] | 0.0.15.0.0.41.118.0.0.257.1.0.0.0.0.0.0.0 | 液温过低
[16 empty] | 0.0.15.0.0.41.118.0.0.258.1.0.0.0.0.0.0.0 | 供水压力过高预警
[16 empty] | 0.0.15.0.0.41.118.0.0.259.1.0.0.0.0.0.0.0 | 掉电报警
[16 empty] | 0.0.15.0.0.41.118.0.0.260.1.0.0.0.0.0.0.0 | 从板通讯故障
[16 empty] | 0.0.15.0.0.41.118.0.0.261.1.0.0.0.0.0.0.0 | 故障状态4
[16 empty] | 0.0.15.0.0.41.118.0.0.262.1.0.0.0.0.0.0.0 | 压机起动瞬间过流
[16 empty] | 0.0.15.0.0.41.118.0.0.263.1.0.0.0.0.0.0.0 | 压机加速运行过流
[16 empty] | 0.0.15.0.0.41.118.0.0.264.1.0.0.0.0.0.0.0 | 压机减速运行过流
[16 empty] | 0.0.15.0.0.41.118.0.0.265.1.0.0.0.0.0.0.0 | 压机恒速运行过流
[16 empty] | 0.0.15.0.0.41.118.0.0.266.1.0.0.0.0.0.0.0 | 压机加速运行过压
[16 empty] | 0.0.15.0.0.41.118.0.0.267.1.0.0.0.0.0.0.0 | 压机减速运行过压
[16 empty] | 0.0.15.0.0.41.118.0.0.268.1.0.0.0.0.0.0.0 | 压机恒速运行过压
[16 empty] | 0.0.15.0.0.41.118.0.0.269.1.0.0.0.0.0.0.0 | 压机待机时过压
[16 empty] | 0.0.15.0.0.41.118.0.0.270.1.0.0.0.0.0.0.0 | 压机运行中欠压
[16 empty] | 0.0.15.0.0.41.118.0.0.271.1.0.0.0.0.0.0.0 | 压机输出缺相
[16 empty] | 0.0.15.0.0.41.118.0.0.272.1.0.0.0.0.0.0.0 | 压机功率器件保护
[16 empty] | 0.0.15.0.0.41.118.0.0.273.1.0.0.0.0.0.0.0 | 压机过热
[16 empty] | 0.0.15.0.0.41.118.0.0.274.1.0.0.0.0.0.0.0 | 压机过载
[16 empty] | 0.0.15.0.0.41.118.0.0.275.1.0.0.0.0.0.0.0 | 压机检测过载
[16 empty] | 0.0.15.0.0.41.118.0.0.276.1.0.0.0.0.0.0.0 | 压机负载过重
[16 empty] | 0.0.15.0.0.41.118.0.0.277.1.0.0.0.0.0.0.0 | 压机速度过大
[16 empty] | 0.0.15.0.0.41.118.0.0.278.1.0.0.0.0.0.0.0 | 故障状态5
[16 empty] | 0.0.15.0.0.41.118.0.0.279.1.0.0.0.0.0.0.0 | 压机D轴电流过大
[16 empty] | 0.0.15.0.0.41.118.0.0.280.1.0.0.0.0.0.0.0 | 压机Q轴电流过大
[16 empty] | 0.0.15.0.0.41.118.0.0.281.1.0.0.0.0.0.0.0 | 压机参数存储失败
[16 empty] | 0.0.15.0.0.41.118.0.0.282.1.0.0.0.0.0.0.0 | 压机通讯异常
[16 empty] | 0.0.15.0.0.41.118.0.0.283.1.0.0.0.0.0.0.0 | 压机电流检测故障
[16 empty] | 0.0.15.0.0.41.118.0.0.284.1.0.0.0.0.0.0.0 | 压机启动中电机堵转
[16 empty] | 0.0.15.0.0.41.118.0.0.285.1.0.0.0.0.0.0.0 | 压机运行中电机堵转
[16 empty] | 0.0.15.0.0.41.118.0.0.286.1.0.0.0.0.0.0.0 | 压机失速故障
[16 empty] | 0.0.15.0.0.41.118.0.0.287.1.0.0.0.0.0.0.0 | 压机中断溢出1
[16 empty] | 0.0.15.0.0.41.118.0.0.288.1.0.0.0.0.0.0.0 | 压机中断溢出2
[16 empty] | 0.0.15.0.0.41.118.0.0.289.1.0.0.0.0.0.0.0 | 压机启动中转子抖动过大
[16 empty] | 0.0.15.0.0.41.118.0.0.290.1.0.0.0.0.0.0.0 | 压机运行中转子抖动过大
[16 empty] | 0.0.15.0.0.41.118.0.0.291.1.0.0.0.0.0.0.0 | PFC过流
[16 empty] | 0.0.15.0.0.41.118.0.0.292.1.0.0.0.0.0.0.0 | PFC峰值电流过大
[16 empty] | 0.0.15.0.0.41.118.0.0.293.1.0.0.0.0.0.0.0 | PFC有效值电流过大
[16 empty] | 0.0.15.0.0.41.118.0.0.294.1.0.0.0.0.0.0.0 | 变频器故障代码
[16 empty] | 0.0.15.0.0.41.118.0.0.295.1.0.0.0.0.0.0.0 | 系统总故障等级
[16 empty] | 0.0.15.0.0.41.118.0.0.296.1.0.0.0.0.0.0.0 | 系统总故障代码
[16 empty] | 0.0.15.0.0.41.118.0.0.297.1.0.0.0.0.0.0.0 | 变频风机故障1
[16 empty] | 0.0.15.0.0.41.118.0.0.298.1.0.0.0.0.0.0.0 | 风机启动瞬间过流
[16 empty] | 0.0.15.0.0.41.118.0.0.299.1.0.0.0.0.0.0.0 | 风机加速运行过流
[16 empty] | 0.0.15.0.0.41.118.0.0.300.1.0.0.0.0.0.0.0 | 风机减速运行过流
[16 empty] | 0.0.15.0.0.41.118.0.0.301.1.0.0.0.0.0.0.0 | 风机恒速运行过流
[16 empty] | 0.0.15.0.0.41.118.0.0.302.1.0.0.0.0.0.0.0 | 风机加速运行过压
[16 empty] | 0.0.15.0.0.41.118.0.0.303.1.0.0.0.0.0.0.0 | 风机减速运行过压
[16 empty] | 0.0.15.0.0.41.118.0.0.304.1.0.0.0.0.0.0.0 | 风机恒速运行过压
[16 empty] | 0.0.15.0.0.41.118.0.0.305.1.0.0.0.0.0.0.0 | 风机待机时过压
[16 empty] | 0.0.15.0.0.41.118.0.0.306.1.0.0.0.0.0.0.0 | 风机运行中欠压
[16 empty] | 0.0.15.0.0.41.118.0.0.307.1.0.0.0.0.0.0.0 | 风机输入缺相
[16 empty] | 0.0.15.0.0.41.118.0.0.308.1.0.0.0.0.0.0.0 | 风机输出缺相
[16 empty] | 0.0.15.0.0.41.118.0.0.309.1.0.0.0.0.0.0.0 | 风机功率器件保护
[16 empty] | 0.0.15.0.0.41.118.0.0.310.1.0.0.0.0.0.0.0 | 风机过热
[16 empty] | 0.0.15.0.0.41.118.0.0.311.1.0.0.0.0.0.0.0 | 变频器过载
[16 empty] | 0.0.15.0.0.41.118.0.0.312.1.0.0.0.0.0.0.0 | 风机过载
[16 empty] | 0.0.15.0.0.41.118.0.0.313.1.0.0.0.0.0.0.0 | 外部故障
[16 empty] | 0.0.15.0.0.41.118.0.0.314.1.0.0.0.0.0.0.0 | 变频风机故障2
[16 empty] | 0.0.15.0.0.41.118.0.0.315.1.0.0.0.0.0.0.0 | 电机负载过重
[16 empty] | 0.0.15.0.0.41.118.0.0.316.1.0.0.0.0.0.0.0 | 变频器欠载
[16 empty] | 0.0.15.0.0.41.118.0.0.317.1.0.0.0.0.0.0.0 | 风扇故障
[16 empty] | 0.0.15.0.0.41.118.0.0.318.1.0.0.0.0.0.0.0 | 用户使用期限禁止时间已到
[16 empty] | 0.0.15.0.0.41.118.0.0.319.1.0.0.0.0.0.0.0 | 参数存储失败
[16 empty] | 0.0.15.0.0.41.118.0.0.320.1.0.0.0.0.0.0.0 | 通讯异常
[16 empty] | 0.0.15.0.0.41.118.0.0.321.1.0.0.0.0.0.0.0 | 电流检测故障
[16 empty] | 0.0.15.0.0.41.118.0.0.322.1.0.0.0.0.0.0.0 | 自整定不良
[16 empty] | 0.0.15.0.0.41.118.0.0.323.1.0.0.0.0.0.0.0 | 模拟输入掉线
[16 empty] | 0.0.15.0.0.41.118.0.0.324.1.0.0.0.0.0.0.0 | PG断线
[16 empty] | 0.0.15.0.0.41.118.0.0.325.1.0.0.0.0.0.0.0 | 热敏电阻开路
[16 empty] | 0.0.15.0.0.41.118.0.0.326.1.0.0.0.0.0.0.0 | 异常停机故障
[16 empty] | 0.0.15.0.0.41.118.0.0.327.1.0.0.0.0.0.0.0 | 三相PFC故障号
[16 empty] | 0.0.15.0.0.41.118.0.0.328.1.0.0.0.0.0.0.0 | 急停
[16 empty] | 0.0.15.0.0.41.118.0.0.329.1.0.0.0.0.0.0.0 | 浪涌
[16 empty] | 0.0.15.0.0.41.118.0.0.330.1.0.0.0.0.0.0.0 | 水浸
[16 empty] | 0.0.15.0.0.41.118.0.0.331.1.0.0.0.0.0.0.0 | 消防
[16 empty] | 0.0.15.0.0.41.118.0.0.332.1.0.0.0.0.0.0.0 | 门禁
[16 empty] | 0.0.15.0.0.41.118.0.0.333.1.0.0.0.0.0.0.0 | Pcs故障反馈
[16 empty] | 0.0.15.0.0.41.118.0.0.334.1.0.0.0.0.0.0.0 | 制冷片故障
[16 empty] | 0.0.15.0.0.41.118.0.0.335.1.0.0.0.0.0.0.0 | 温湿度传感器故障
[16 empty] | 0.0.15.0.0.41.118.0.0.336.1.0.0.0.0.0.0.0 | 制冷片冷端温度传感器故障
[16 empty] | 0.0.15.0.0.41.118.0.0.337.1.0.0.0.0.0.0.0 | 风扇故障
[16 empty] | 0.0.15.0.0.41.118.0.0.338.1.0.0.0.0.0.0.0 | EMS切手动保护
[16 empty] | 0.0.15.0.0.41.118.0.0.339.1.0.0.0.0.0.0.0 | 电表故障
[16 empty] | 0.0.15.0.0.41.118.0.0.340.1.0.0.0.0.0.0.0 | 动环保护
[16 empty] | 0.0.15.0.0.41.118.0.0.341.1.0.0.0.0.0.0.0 | 自定义提示1
[16 empty] | 0.0.15.0.0.41.118.0.0.342.1.0.0.0.0.0.0.0 | 自定义提示2
[16 empty] | 0.0.15.0.0.41.118.0.0.343.1.0.0.0.0.0.0.0 | 自定义提示3
[16 empty] | 0.0.15.0.0.41.118.0.0.344.1.0.0.0.0.0.0.0 | 自定义停机1
[16 empty] | 0.0.15.0.0.41.118.0.0.345.1.0.0.0.0.0.0.0 | 自定义停机2
[16 empty] | 0.0.15.0.0.41.118.0.0.346.1.0.0.0.0.0.0.0 | 自定义停机3
[16 empty] | 0.0.15.0.0.41.118.0.0.347.1.0.0.0.0.0.0.0 | 自定义告警
[16 empty] | 0.0.15.0.0.41.118.0.0.348.1.0.0.0.0.0.0.0 | PCS功率反馈异常
[16 empty] | 0.0.15.0.0.41.118.0.0.349.1.0.0.0.0.0.0.0 | 总消防
[16 empty] | 0.0.15.0.0.41.118.0.0.350.1.0.0.0.0.0.0.0 | 外部消防
[16 empty] | 0.0.15.0.0.41.118.0.0.351.1.0.0.0.0.0.0.0 | 本机消防
[16 empty] | 0.0.15.0.0.41.118.0.0.352.1.0.0.0.0.0.0.0 | 温控系统异常
[16 empty] | 0.0.15.0.0.41.118.0.0.353.1.0.0.0.0.0.0.0 | 自定义提示告警
[16 empty] | 0.0.15.0.0.41.118.0.0.354.1.0.0.0.0.0.0.0 | 自定义重要告警
[16 empty] | 0.0.15.0.0.41.118.0.0.355.1.0.0.0.0.0.0.0 | 自定义严重告警
[16 empty] | 0.0.15.0.0.41.118.0.0.356.1.0.0.0.0.0.0.0 | DOD保护
[16 empty] | 0.0.15.0.0.41.118.0.0.357.1.0.0.0.0.0.0.0 | 直流总压异常
Note on R2: ZeKunZhang: Prompt参考: 根据下面输入的量测数据项各分项的配置，为这个数据项起一个名字，参考格式：【15 min递增间隔数据前向有功电能 （kW·h）】：

## ReadingTypeID其他
mRID | [15 empty] | KAIFA Project | EMS-01 | ReadingType
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | mRID | Description | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
mRID | [17 empty] | macroPeriod 宏周期 | aggregate 聚合方式 | measurePeriod 测量周期 | accumulationBehaviour 累加方式 | flowDirection 流动方向 | commodity 能源分类 | measurementKind 测量类别 | harmonic 谐波 | argument 测量序号 | TOU 分时段号 | CPP 临界峰值 | Tier 分阶梯号 | Phase 相 | multiplier 公乘因子 | uom 统一计量单位 | currency 货币计量单位
8 | 0 | 0 | 1 | 0 | 0 | 3 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 8.0.0.1.0.0.3.0.0.0.0.0.0.0.0.0.0.156 | 人民币（元） | 8.billingPeriod | 0.none | 0.none | 1.bulkQuantity | 0.none | 0.none | 3.currency | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 156.CNY
0 | 0 | 0 | 6 | 0 | 40 | 46 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0.0.0.6.0.40.46.0.0.0.0.0.0.0.0.0.23.0 | 天气温度(℃) | 0.none | 0.none | 0.none | 6.indicating | 0.none | 40.weather | 46.temperature | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 23.degrees Celsius | 0.None
0 | 0 | 0 | 6 | 0 | 40 | 156 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0.0.0.6.0.40.156.0.0.0.0.0.0.0.0.0.281.0 | 湿度（RH） | 0.none | 0.none | 0.none | 6.indicating | 0.none | 40.weather | 156.relativeHumidity | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 281.Relative humidity | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.1.1.0.0.0.0.0.0.0 | 单体最高温度序号 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 1.1.n1 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 7 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.7.0.0.0.0.0.0.0.0.0.0.0 | 时间日期类 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 7.date | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 6 | 0 | 41 | 46 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0.0.0.6.0.41.46.0.0.0.0.0.0.0.0.0.23.0 | 设备温度 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 41.device | 46.temperature | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 23.degrees Celsius | 0.None
0 | 0 | 0 | 6 | 0 | 4 | 46 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0.0.0.6.0.4.46.0.0.0.0.0.0.0.0.0.23.0 | 空气温度 | 0.none | 0.none | 0.none | 6.indicating | 0.none | 4.air | 46.temperature | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 23.degrees Celsius | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.2.1.0.0.0.0.0.0.0 | 单体最低温度序号 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 2.1.n2 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.3.1.0.0.0.0.0.0.0 | 单体最高电压序号 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 3.1.n3 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.4.1.0.0.0.0.0.0.0 | 单体最低电压序号 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 4.1.n4 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.5.1.0.0.0.0.0.0.0 | 编号类5 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 5.1.n5 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.6.1.0.0.0.0.0.0.0 | 编号类6 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 6.1.n6 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.7.1.0.0.0.0.0.0.0 | 编号类7 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 7.1.n7 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.8.1.0.0.0.0.0.0.0 | 编号类8 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 8.1.n8 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.9.1.0.0.0.0.0.0.0 | 编号类9 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 9.1.n9 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 92 | 0.0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0.0.0.0.0.92.0.0.10.1.0.0.0.0.0.0.0 | 编号类10 | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 92.assetNumber | 0.0.none | 10.1.n10 | 0.none | 0.none | 0.none | 0.none | 0.Not applicable or "×1" | 0.N/A | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 64 | 3 | 63 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.64.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 64.phaseB | 3.k | 63.var | 0.None
0 | 0 | 0 | 6 | 4 | 1 | 37 | 0.0 | 0.0 | 0 | 0 | 0 | 32 | 3 | 63 | 0 | 0.0.0.6.4.1.37.0.0.0.0.0.0.0.32.3.63.0 |  | 0.none | 0.none | 0.none | 6.indicating | 4.net | 1.electricity SecondaryMetered | 37.power | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 32.phaseC | 3.k | 63.var | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0.0 | 0 | 0 | 0 | 0 | –24 | 2 | 0 | 0.0.0.0.0.0.0.0.0.0.0.0.0.0.0.–24 .2.0 |  | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.none | 0.0.none | 0.0.none | 0.none | 0.none | 0.none | 0.none | –24 .y | 2.metre | 0.None
Note on R2: ZeKunZhang: Prompt参考: 根据下面输入的量测数据项各分项的配置，为这个数据项起一个名字，参考格式：【15 min递增间隔数据前向有功电能 （kW·h）】：

## Other dict. (hidden)
Index 15 | argumentNumerator 分子参数 | Comments | Index 16 | cpp 临界峰值 | Comments | Index 17 | currency 货币计量单位 | Comments
0.0 | none | Not Applicable | 0 | none | Not Applicable | 0 | None | N
1.2 | n½ | One-half | 1 | cppA | Consumption associated with critical peak period A | 36 | AUD | Australian Dollar
0.1 | n0 | “Zero” (for systems that use zero based numbering schemes) | 2 | cppB | Consumption associated with critical peak period B | 124 | CAD | Canadian Dollar
1.1 | n1 | "One,” where the measure needs an argument such as CEMI(n=1) | 3 | cppC | Consumption associated with critical peak period C | 156 | CNY | Chinese Yuan Renminbi
2.1 | n2 | "Two" where the measure needs an argument such as CEMI(n=2) | 4 | cppD | Consumption associated with critical peak period D | 208 | DKK | Danish Crown
3.1 | n3 | "Three" where the measure needs an argument such as CEMI(n=3) | 5 | cppE | Consumption associated with critical peak period E | 356 | INR | India Rupee
4.1 | n4 | "Four" where the measure needs an argument such as CEMI(n=4) | 6 | cppF | Consumption associated with critical peak period F | 392 | JPY | Japanese Yen
5.1 | n5 | "Five" where the measure needs an argument | 7 | cppG | Etc. | 578 | NOK | Norwegian Crown
6.1 | n6 | Six |  |  |  | 643 | RUB | Russian Ruble
7.1 | n7 | Seven |  |  |  | 710 | ZAR | South African Rand
8.1 | n8 | Eight |  |  |  | 752 | SEK | Swedish Krona
9.1 | n9 | Nine |  |  |  | 756 | CHF | Swiss Franc
10.1 | n10 | Ten |  |  |  | 826 | GBP | British Pound
15.1 | n15 | Fifteen |  |  |  | 840 | USD | US Dollar
30.1 | n30 | Thirty |  |  |  | 978 | EUR | Euro
45.1 | n45 | Fourtyfive
60.1 | n60 | Sixty
120.1 | n120 | 2 × 60 = 120
155.1 | n155 | One hundred fifty five
240.1 | n240 | 4 × 60 = 240
305.1 | n305 | Three hundred and five.
360.1 | n360 | 6 × 60 = 360
480.1 | n480 | 8 × 60 = 480
720.1 | n720 | 12 × 60 = 720
720.60 | n720/60 | 12 × 60/1 × 60
720.120 | n720/120 | 12 × 60/2 × 60
720.180 | n720/180 | 12 × 60/3 × 60
720.240 | n720/240 | 12 × 60/4 × 60
720.360 | n720/360 | 12 × 60/6 × 60